General Description

Water cooled chiller with heat pump operation option designed to meet the most demanding energy efficiency requirements and exceed the minimum acceptable performance characteristics dictated by EU Regulation 2016/2281. Unit shall be of compact arrangement intended for indoor installation, able to be connected to a dry-cooler or
water-cooling tower. Chiller shall operate on environment-friendly R134a refrigerant and be equipped with either one (1) or two (2) independent cooling circuits. Each chiller shall be equipped with either two (2), three (3) or four (4) twin-turbine centrifugal magnetic levitation compressors depending on unit size. Unit shall feature self-adjusting electronic operational control via a dedicated touch-screen control interface. Chiller shall be designed, produced and tested at an ISO 9001, ISO 14001 and ISO 50001 certified plant. Unit to be Eurovent certified.

| Ecodesign Requirements for Water Cooled Chillers (EU Regulation 2016/2281) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cooling | January 2018 |  | January 2021 |  |
|  | ηs,c % Primary Energy | SEER/SEPR | ηs,c % Primary Energy | SEER/SEPR |
| Comfort Chillers Capacity: 400 to 1,499 kW | 227 | 5.75 | 252 | 6.38 |
| Comfort Chillers Capacity: 1,500 to 2,000 kW | 245 | 6.20 | 272 | 6.88 |
| High-Temperature Process Chillers Capacity: 400 to 1,499 kW | - | 7.50 | - | 8.00 |
| High-Temperature Process Chillers Capacity: 1,500 to 2,000 kW | - | 8.00 | - | 8.50 |
| Medium-Temperature Process Chillers Capacity: Greater than 300 kW (effective as of July 2018) | - | 4.37 | - | - |

Unit Operating Limits

Unit should meet the following minimum operating limit requirements:

| Evaporator | Minimum | Maximum |
| --- | --- | --- |
| Entering Water Temperature at start-up (°C) | - | 35.0 |
| Leaving Water Temperature during operation (°C) | 3.3 | 20.0 |
| Entering/Leaving Water Temperature Difference (K) | 3.0 | 11.1 |
| Condenser | Minimum | Maximum |
| Entering Water Temperature at start-up (°C) | 13.0 | - |
| Leaving Water Temperature during operation (°C) | 14.0 | 50.0 |
| Entering/Leaving Water Temperature Difference (K) | 3.0 | 11.1 |
| Minimum Unit Handing Temperature (°C) | -20 |  |
| Maximum Unit Handling Temperature (°C) | 66 |  |

Directive Compliance

Product shall comply with the following directives and standards:

- Machinery Directive 2006/42/EC.

- Electromagnetic Compatibility Directive 2014/30/EU.

- EMC immunity and emissions EN 61800-3 'C2'.

- Low Voltage Directive 2014/35/EU.

- RoHS 2011/65/EU.

- Pressure Equipment Directive (PED) 2014/68/EU.

- Machinery Directive EN 60-204 -1.

- Refrigeration systems and heat pumps EN 378-2.

- Regulation (EU) 2016/2281 implementing Directive 2009/125/EC (Ecodesign).

Unit Specification

Unit technical characteristics:

- Cooling capacity: …… kW

- Electrical power consumption: …… kW

- Heating capacity: …… kW

- Minimum Net EER at full load conditions according to EN14511:3-2013: …… kW/kW

- Minimum Net COP at full load conditions according to EN14511:3-2013: …… kW/kW

- Minimum Eurovent-certified SEER according to Ecodesign Regulation 2016/2281: …… kW/kW

- Minimum SCOP according to EN 813/2013: …… kW/kW

- Evaporator chilled water entering/leaving temperature: …… / …… °C

- Evaporator pressure drop: …… kPa

- Secondary fluid: ……

- Condenser hot water entering/leaving temperature: …… / …… °C

- Condenser pressure drop: …… kPa

- Secondary fluid: ……

- CO2 equivalent: …… tonnes

Chiller shall be delivered with Ecodesign conformity sheets. Conformity sheets shall include a unit life cycle analysis section. Chiller shall be capable of start-up operation with a condenser entering water temperature of 13°C 
(when equipped with low condensing temperature control option). Unit shall be capable of starting up with an evaporator entering water temperature of at least 35°C.

Component Description

Casing

Heat exchangers and compressors to be housed in a single autonomous structure. Chiller electrical cabinet shall be coated with light grey RAL 7035 paint.

Compressors

Unit shall be equipped with two-stage IP54 centrifugal compressors driven by permanent-magnet synchronous variable speed motors with integrated overheating protection system. Inverter motors shall be of high power factor (cosφ>0.9 for main operating conditions), able to enforce unit linear stepless capacity control (up to 36,000 rpm). Compressor capacity control by means of successive use of swept volume variation shall ensure that capacity demands are met with precision, achieving great efficiency at partial loads. Compressors shall be of oil-free type eliminating the need for a lubrication system, simplifying the pipping connections and improving exchanger performance due to the elimination of the oil film between the refrigerant and heat exchanger surfaces. Compressors shall be equipped with magnetic levitation bearings to eliminate friction between mechanical components, hence increasing compressor lifetime. The placing of magnetic levitation bearings shall also maximize noise reduction and eliminate component vibration. Compressors shall be equipped with an inlet guide valve at turbine suction and integrated soft-starter able to limit starting current to 5A.
Motor and electronic power section shall be refrigerant-cooled. Full electronic motor protection against thermal and electrical overload shall be realized by use of internal sensors. Sensors on refrigerant suction and discharge shall also be fitted for temperature monitoring. Overpressure safety and check valves shall be fitted to prevent fluid reverse rotation while compressor is in transition period. Optionally shut-off service valves shall be placed on evaporator inlet and compressor suction to allow for unit maintenance operations to take place.

Evaporator

Chiller shall be equipped with a single, high-performance, glandless-type evaporator made of copper tube bundles with internal and external grooves. Evaporator design shall feature either one (1) or two (2) independent cooling circuits. Two entering and leaving water temperature sensors shall be used to monitor fluid temperature. Evaporator heat insulation shall be made of shaped cellular foam, at least 19 mm thick. Evaporator hydraulic connections shall be of victaulic type to ensure quick and watertight concealment. Maximum operating pressure on evaporator water side shall be at least
10 bar. Evaporator shall be equipped with an electronic flow controller. Paddle-type sensors and differential pressure controllers shall not be acceptable. Several choices of evaporator hydraulic connections shall be available to adapt to all possible constraints.

Condenser

Unit shall be equipped with a single condenser made of copper tube bundles with internal and external grooves. Condenser design shall feature either one (1) or two (2) independent cooling circuits. Two entering and leaving water temperature sensors shall be used to monitor fluid temperature. Condenser heat insulation shall be made of shaped cellular foam, at least 19 mm thick. Condenser hydraulic connections shall be of victaulic type to ensure quick and watertight concealment between unit and hydraulic system connections. Maximum operating pressure on condenser shall be at least 10 bar.

Safety Devices

Each cooling circuit shall be equipped with the following accessories:

- Two (2) electronic expansion valves.

- One (1) liquid sight glass to inspect refrigerant condition.

- Check-valve to prevent compressor fluid recirculation during transition.

- High- and low- pressure sensors.

- Pressure safety valves on refrigerant circuit.

- High pressure switch on each compressor.

- Evaporator anti-frost protection sensor.

- Factory-fitted electronic water flow controller.

Electric Cabinet

Electric cabinet shall be made of pre-painted steel metal sheets with an IP23 protection rating. Cabinet shall be equipped with EMC filters and line reactors. Cabinet power supply shall be three-phased, 400 V (+10/-10%) 50 Hz + Earth
(without neutral). Electric cabinet shall feature a main external safety switch as well as a 24V control circuit supply transformer. Secure technician access to the electric cabinet shall be realized by use of door contact switches. The internal wiring of the cabinet shall be numbered and all electrical components shall be marked. Optionally the cabinet shall be equipped with a control power supply circuit for the regulation of a single external pump on the evaporator and/or condenser side.

Unit Control

Chiller control system shall feature a 7-inch touchscreen display equipped with a user-friendly operator interface enabling intuitive navigation using icons.

User Interface

- 7-inch touchscreen colour display.

- Unit parameter configuration (3 access levels, User/Maintenance/Factory, all password-protected).

- Display of trend curves for main operating parameters.

- Menu available in nine (9) languages. One (1) additional local language may be added.

- Capacity to load a custom translation file.

- Interface access through web browser.

Control Features

Unit control system shall be able to perform the following functions:

- Water temperature control.

- Capacity to vary unit setpoint according to outdoor temperature.

- Management of second setpoint.

- Compressor control: start-up sequencing, metering and operation time balancing.

- Compressor short-cycle protection management.

- Component protection against phase reversion.

- Chiller weekly and hourly time schedule. Capacity to add up to sixteen (16) absence periods.

- Condensing pressure limitation.

- Fault diagnosis and operating status display.

- Fault memory management allowing for the last fifty (50) recorded incidents to be assessed. Control system shall automatically record main operating parameter values when a system fault occurs.

- Master/slave management capacity of two units connected in parallel. Capacity to perform operating time balancing and automatic unit changeover should a fault occur on one of the two units.

- Capacity to add up to two (2) user e-mail addresses for the automatic submission of fault reports.

Maintenance Function

Controller shall have two maintenance reminder functions intended to make the user aware of the need to regularly service the equipment to ensure smooth unit operation.

- Periodic reminder: this function shall be used to select the period between two maintenance checks.

- Mandatory F-GAS sealing test reminder: this function shall be activated by default and shall be used to select the period between two sealing tests depending on the refrigerant charge of the chiller in accordance with F-GAS regulations.

Remote Control

- Capacity to communicate with CMS via MODBUS/JBS TC/IP output.

- Control via built-in web server to remotely access all HMI functions via a PC with alarm notifications via email alerts.

- Option to equip remote controller with factory-fitted bidirectional communication system using the BACnet over Ethernet IP network protocol. This option shall be used to integrate the unit into a BACnet IP centralised building management system.

- Volt-free contacts shall also be available on unit remote controller:

  - Inputs:

    - Automatic operation control: unit ON/OFF switch.

    - Heating/cooling operation mode selection.

    - Setpoint selection: activates a second setpoint.

    - Setpoint offset: 4-20 mA signal to offset unit active setpoint.

    - Condenser flow switch.

    - Power limitation (4-20 mA to set demand limit): allows the power consumption of the machine to be limited by stopping one or more compressors.

    - End of storage signal: enables return to the second setpoint at the end of the storage cycle.

    - Fault report.

    - Customer interlock (open = unit shuts down/closed = unit operates).

    - Time schedule override: cancels time schedule.

  - Outputs:

    - Alarm relay (report alarm state).

    - Operational status reporting: indicates that the unit is in production mode by 0-10V command.

    - Alert reporting: this contact indicates the presence of a minor fault which has not caused the affected circuit to stop.

    - Fault reporting: indicates the presence of a major fault which has caused one or both refrigerating circuits to stop.

    - Power indication: analogue output (0-10 V) providing an indication of the machine's load rate.

    - Compressor status.

ηs,c=SEER kWhkWh×1002.50-icorrections

Comfort chiller SEER calculated at 12 oC/7 oC chilled water entering/leaving temperature.

High-Temperature chiller SEPR calculated at 12 oC/7 oC chilled water entering/leaving temperature.

Medium-Temperature chiller SEPR calculated at -2 oC/-8 oC chilled water entering/leaving temperature.

Minimum acceptable SEPR values for Medium-Temperature chillers may be reduced by up to 10% should unit be	charged with refrigerant that has a GWP<150.