General description

Factory assembled single piece water-cooled chiller, shall include all factory wiring, piping, controls, refrigerant charge (R-134a), dual refrigeration circuits, screw compressors, electronic expansion valves and equipment required prior to field start-up.

Quality assurance

Unit shall be rated in accordance with Eurovent standard.

Unit construction shall comply with European directives:

- Pressurised equipment directive (PED) 97/23/EC

- Machinery directive 98/37/EC, modified

- Low voltage directive 73/23/EEC, modified

Electromagnetic compatibility directive 89/336/EEC,

modified, and the applicable recommendations of

European standards:

- Machine safety: electrical equipment in machines, general

regulations, EN 60204-1

- Electromagnetic emission EN 50081-2

- Electromagnetic immunity EN 50082-2.

Unit shall be designed, manufactured and tested in a facility with a quality management system certified ISO 9001 and environmental management system ISO 14001.

Unit shall be run tested at the factory..

Design performance data

- Cooling capacity (kW): ……

- Unit power input (kW): ……

- Full load energy efficiency, EER (kW/kW): ……

- Eurovent Class ………

- Part load energy efficiency, ESEER (kW/kW): ……

- Evaporator entering/leaving water temperature (°C): … /

- Fluid type: …….

- Fluid flow rate (l/s): ……

- Evaporator pressure drops (kPa): ……

- Condenser entering/leaving water temperature (°C): ……

- Fluid type: …….

- Fluid flow rate (l/s): ……

- Condenser pressure drops (kPa): ……

- Sound power level at full load (dB(A)): ……

- Dimensions, length x depth x height (mm): … x … x

- Number of compressors

The unit shall be capable of starting with up tp 13 °C entering water temperature to the condenser. The unit shall be capable of starting with up to 25 °C entering water temperature to the evaporator.

Compressors

- Semi-hermetic twin-screw compressors with internal muffler and check valve.

- Each compressor shall be equipped with a discharge shutoff valve.

- Capacity control shall be provided by pilot-operated solenoid valve, capable of reducing unit capacity to 20% of full load. Compressor shall start in unloaded condition.

- Motor cooling shall be provided by direct liquid injection and protected by internal overload thermistor.

- Lube oil system shall include pre-filter and internal filter capable of filtration to 3 microns.

Evaporator

- Unit shall be equipped with a single evaporator.

- Shall be manufactured, tested and stamped in accordance with the European directive for pressurised equipment 97/23/EC. The maximum refrigerant-side operating pressure will be 2500 kPa, and the maximum water-side pressure will be 1000 kPa.

- Shall be mechanically cleanable shell-and-tube type with removable heads.

- Tubes shall be internally-enhanced, seamless-copper type, and shall be rolled into tube sheets.

- Shall be equipped with Victaulic water connections (water connection kit on demand).

- Shell shall be insulated with 19-mm closed-cell, polyurethane foam with a maximum K factor of 0.28 W / m2.Κ

- Shall have an evaporator drain and vent.

- Design shall incorporate 2 independent refrigerant circuits.

- Shall incorporate a refrigerant level control system.

Condenser

- Unit shall be equipped with a single condenser.

- Shall be manufactured, tested and stamped in accordance with the European directive for pressurised equipment 97/23/EC.

- The maximum refrigerant-side operating pressure will be 2500 kPa, and the maximum water-side pressure will be 1000 kPa.

- Shall be mechanically cleanable shell-and-tube type with removable heads.

- Tubes shall be internally-enhanced, seamless-copper type, and shall be rolled into tube sheets.

- Shall be equipped with Victaulic water connections

- Design shall incorporate two independent refrigerant circuits and the oil separator.

Refrigerant circuit

Every Refrigerant circuit components shall include oil separators, high and low side pressure relief devices (according to applicable standards), discharge and liquid line shutoff valves, filter driers, moisture indicating sight glasses, expansion devices, refrigerant economizers (unit sizes 190, 285, 375), and complete operating charge of both HFC-134a refrigerant and compressor oil.

Electrical characteristics

- Unit electrical power supply shall enter the unit at one (30HX 080-190) or two locations.

- Unit shall operate on 3-phase power supply without neutral.

- Unit shall have a factory-installed, star-delta starter to limit electrical inrush current.

- Control voltage shall be supplied by a factory installed transformer.

- Unit shall be supplied with factory-installed, electrical disconnect switch/circuit breaker.

Controls

Unit controls shall include as a minimum: the microprocessor, the LOCAL/OFF/REMOTE/CCN selector and a 6-digit diagnostic display (scroll-down text) with keypad. It shall be capable of performing the following functions:

- Automatic change-over between the main compressor and the non-active compressor(s).

- Capacity control based on leaving chilled fluid temperature with return fluid temperature sensing.

- Limit the chilled fluid temperature pull-down rate at start-up to an adjustable range of 0.1°C to 1.1°C per minute to prevent excessive demand spikes at start-up.

- Enable adjustment of leaving chilled water temperature according to the return water temperature or by means of a 0-10 V signal.

- Provide a dual set point for the leaving chilled water temperature activated by a remote contact closure signal.

- Enable a two-level demand limit control (between 0 and 100%), activated by a remote contact closure or a 0 to 10 V signal.

- Control evaporator water pump, safety pump (if installed), and the condenser pump.

- Enable automatic changeover in the main phase or shutdown of two chillers in a single system.

- With two time scheduling programs enable unit startup control and set-point change

Diagnosis

- Display module shall be capable of displaying set points, system status (including temperatures, pressures, currents for each compressor, run times and percent loading), and any alarm or alert conditions.

- The control shall allow a quick test of all machine elements to verify the correct operation of every switch, circuit breaker, contactor etc. before the chiller is started.

- The control shall be capable of balancing the compressor operating times and the number of compressor startups.

- EXV control, based on throttling (Carrier patent) optimises evaporator charging, ensuring condenser superheat and subcooling.

Safeties

Control system shall provide the unit with protection against the following:

- Reverse rotation

- Low chilled water temperature

- Low oil pressure (per compressor)

- Current imbalance

- Compressor thermal overload

- High pressure (with automatic compressor unloading in case of excessive condensing temperature)

- Electrical overload and short circuit

- Loss of phase, undervoltage and power supply failure

- Απώλεια φάσης , υπόταση και απώλεια παροχής τάσης.