General description

Air cooled water reversible heat pumps for indoor installation equipped with centrifugal fan (STD version) or electronic plugfan (HEE version), plate exchanger, hermetic scroll compressor, and electronic control with microprocessor and operating with R-410A refrigerant.

The unit will be supplied with an integrated circulation pump: 30PΗC

Quality assurance

Unit construction shall comply with European directives:

- Machine safety: electrical equipment in machines, general requirements EN 60-204 - EN 378-2

- Machinery directive 2006/42 CE- CEM

- Electromagnetic compatibility directive 2004/108/CE - DBT

- Low voltage directive 2006/95 CE - DESP

- 14/068 CE (Category 2).

Unit shall be run tested at the factory , verifying the correct operation of all their components.

Unit shall be designed, manufactured and tested in a facility with a quality management system certified ISO 9001 and environmental management system ISO 14001.

Design performance data

- Cooling capacity (kW): ……

- Heating capacity (kW): ……

- Unit power input (kW): ……

- Part load energy efficiency, ESEER (kW/kW): ……

- Part load l energy efficiency in heating, SCOP (kW/kW): ……

- Full load energy efficiency, EER (kW/kW): ……

- Full load energy efficiency in heating, COP (kW/kW): ……

- Evaporator entering/leaving water temperature (°C): … /

- Evaporator entering/leaving water temperature (heating) (°C): … /

- Fluid type: …….

- Fluid flow rate (l/s): ……

- Evaporator pressure drops (kPa): ……

- Outdoor air temperature (°C): ……

- Outdoor air temperature (heating) (°C): ……

- Sound power level at full load (dB(A)): ……

- Dimensions, length x depth x height (mm): … x … x

The unit shall operate at full load with ambient temperatures ranging from 12 °C to 46 °C , with evaporator leaving liquid temperature between 5°C and +18 °C in cooling mode and ambient temperatures ranging from -15 °C to 20 °C , with evaporator leaving liquid temperature between 30°C and +55 °C in heating mode

Frame

Chassis made of galvanised steel metal. Painted in oven-baked polyester powder paint in light grey colour (RAL 7035). Self-supporting and isolated frame.

Compressor

Unit shall have Hermetic scroll-type compressor, with acoustic insulating cover, assembled over antivibration mounts. Control of phase equilibrium and the direction of rotation.

The scroll type compressor have the following safeties:

- Non-return valve built into the compressor.

- Thermal protection in the compressor, which stops the operation of the motor when there is excessive heating.

- Protection of the compressor discharge temperature through a klixon.

Evaporator

Stainless steel (AISI-316 ) plate heat exchanger with copper and silver welding connections.

The evaporator has one refrigerant circuit and includes thermal foam insulation.

Water anti-freeze protection

This safety device is built into the electronic control. This is activated in COOLING mode when the water outlet temperature is lower than the set value. This causes the stop of the outdoor fan and the compressor.

Anti-freeze protection with heaters (optional)

Anti-freeze protection with fl exible electrical heaters around the pipe lines of the hydraulic circuit to avoid their freezing. This optional is recommended with negative temperatures.

The minimum outlet temperature for the unit will be +5ºC with pure water and -10ºC with glycol water.

Condenser

Condenser coils shall be made of copper pipes and aluminium fins and condensate drain pan.

The air supply position can be either horizontal or vertical.

(options) Coils protection:

- Coil with copper pipes and copper fi ns (upon request).

- Coil with copper pipes and aluminium fins with polyurethane and blygold coating.

- Electrical heaters in the condensate drain pan. Mandatory when outdoor temperatures are below 3°C.

- Operation with glycol water up to a minimum outlet temperatureof -10ºC.

Fans:

STD Version (Standard):

- Centrifugal fan coupling by pulleys and belts.

- Electric motor with tensioner, energy-effi cient IE2 motors, class F, IP55, and internal thermal protection.

- One double-intake turbine, with an impeller with front-curved blades. Greased spherical bearings, with no maintenance required.

- Choice of available pressure from 7 to 35 mm.w.c.

HEE Version (High Energy Effi ciency):

- Variable speed electronic plug-fan(s) with condensation pressure control which adapt their rotation speed to the installation requirements, thereby reducing electricity consumption, the sound level at partial charge, and improving the average seasonal output of the unit (ESEER).

- Energy-effi cient ErP 2015 motor, Class F, IP54, and internal thermal protection.

(option) Μotorized damper

In units ( STD Version) that work in cooling with an outdoor temperature lower than 12ºC, the condensation pressure control allowing an “all seasons” operation (up to -15ºC) is mandatory. This is performed per motorized damper in the fan outlet.

A servomotor opens or closes the damper depending on the proportional signal 0-10V received from the electronic control system (during the operation of the fan).

Refrigerant circuit

The unit consist of one refrigerant circuit which iclude:

- Crankcase heater.

- Thermostatic expansion valve with external equalisation.

- Anti-acid dehydrating filter.

- Complete operating charge of refrigerant R-410a.

- Liquid receiver.

- Four-way cycle reversing valves.

Electric panel

- Complete and fully wired electric panel. Insulated panel cover to prevent condensation.  IP55 protection.

- Power supply with neutral and main ground connection.

- Compressor and fan motor contacts.

- (option) Compressor soft starter.

- (option) Transformer for power supply without neutral.

- (option) Voltage 400 / 440V - 60 Hz (upon request).

- (option) Energy meter for monitoring of the power consumption of the installation.

Control

The control l is basically comprised of a μPC SMALL control board, a pGD1 graphic terminal, a TCO user terminal (optional for remote control) and sensors.

This control allows the connection to a centralised technical management system by using a specifi c BMS card for some of the following communication protocols: Carel, Modbus, LonWorks®, BACnetTM MSTP, Konnex, Modbus TCP/IP, BACnetTM Ethernet, TCP/ IP, SNMP V1-2-3, FTP and HTTP.

The main functions are:

- Control in COOLING / HEATING modes.

- Selecction of inlet water temperature setpoints for COOLING / HEATING modes.

- Permanent control and optimization of the operating parameters

- Safety management.

- Timing of the compressor.

- Defrosting management .

- Control of condensation and evaporation pressures.

- Control of outdoor electronic plug-fan (HEE version).

- Control of the circulation pump.

- Regulation of the water outlet temperature.

- Compensation of the setpoint based on the outdoor temperature.

- Timer and weekly programming.

- Failure diagnosis and main alarm.

TCO user terminal (optional for remote control):

The TCO user terminal, for remote control, allows:

- Modification of some operating parameters.

- Unit ON / OFF.

- Selection of the operating mode and setting of setpoints.

- On-screen display some controlled variables and probe values.

- On-screen display of alarms codes.

Evaporator hydronic module (30PAC)

The hydronic module shall be integrated in the chiller and includes  the following components:

- Monocellular IP55 centrifugal circulation pump that can operate with glycol water (mono-ethylene glycol). The pump must be changed for

- mono-propylene glycol (upon request).

- Closed expansion vessel.

- Safety valve with a tare value of 4 bar and draining valve.

- Air bleeder valve (model 160HEE and 180HEE).

- Water Filter with stainless steel mesh (500 microns), supplied in the kit for installation by the installer.

The pump installed in a unit 30PAC/PHC can be replaced for:

- - High-pressure, monocellular, IP55, circulation pump that can operate with glycol water (mono-ethylene glycol).

- - Low-pressure, monocellular, IP55, circulation pump that can operate with glycol water (mono-ethylene glycol) (except model 90).

- (option) Anti-freeze protection with flexible electrical heaters around the pipe of the hydraulic circuit.

Safeties

The unit will  have the necessary control and safety elements;

- Differential pressure switch for control of water flow.

- Water anti-freeze protection built into the control, depending on the temperature measured by the probe placed on the exchanger outlet.

- Refrigerant anti-freeze protection.

- Compressor discharge temperature control.

- Non-return valve built into the compressor discharge.

- Compressor thermal protection.

- Main door switch.

- Automatic switch in the control circuit.

- Magnetothermic protection switches for the compressor and fan motor power line.

- Timing the disconnection of the circulation pump.

- Failure safety device for the circulation pump.

Installation options

- Antivibration mounts made of rubber.

- Protection grille for the coil.

- Gravimetric filters in the return air. The fi lters frame is removable, and upon request, it is possible to supply the frame independently with the unit, to be joined on site.

- Flexible ducts for supply and return air.

- Flexible hydraulic connections (500mm), supplied in the kit.

Available for:

- Inlet / outlet of the unit.

- Inlet / outlet of the desuperheater circuit.

- - For 30PA/PH units, filter with stainless steel mesh (500 microns), supplied in the kit.

Note: this filter is standard for 30PAC/PHC units.

- Cut-off and water control valves, supplied in the kit.

- High-pressure and low-pressure gauges in the cooling circuit.

Energy recovery

The unit includes a desuperheater circuit that allows the production of hot water at a temperature greater than in the condensation circuit.

Desuperheater can be used either on cooling or heating mode.

For the same cooling or heating capacity, the desuperheater system allows a free heating of hot water with a reduction of the total input power of the unit.

Desuperheater circuit includes:

- - Thermally isolated, welded stainless steel plate exchanger for working in a closed circuit in the recovery of hot gases.

- - Draining valve and ball valve

- - Hot water recovery control thermostat.

- - Option for a 3-speed hot water circulation pump.