Product specifications in italic shall be considered as key requirements.

SYSTEM DESCRIPTION

Factory assembled air to water chiller utilizing rotary or scroll compressors, fixed-speed fans and optional hydronic pump module. The unit shall include all necessary wiring, piping, charge of R410A refrigerant, microprocessor controls.

Note: Hydronic pump module shall be available with variable-speed driven pump and include all the necessary components as described in hydronic module option.

For better efficiency and to be in accordance with ECODESIGN’s rules, hydronic modules shall include a class A variable speed circulator. This circulator allows a power input reduction and offers better available pressure for small sizes.

QUALITY ASSURANCE

Unit shall be rated in accordance with EN14511-3 Standard, latest revision and unit performances shall be certified by independent Eurovent certification body. Unit without independent Eurovent certification shall be excluded.

Unit construction shall comply with European directives:

- Commission regulation (EU) N°327/2011 implementing Directive 2009/125/EC with regards to Eco-design requirements for industrial fans.

- Commission regulation (EU) N°640/2009 implementing Directive 2009/125/EC with regards to Eco-design requirements for electric motors.

- Commission regulation (EU) N°547/2012 implementing Directive 2009/125/EC with regards to Eco-design requirements for water pumps (Unit equipped with hydronic module option).

- Pressurized equipment directive (PED) 97/23/EC.

- Machinery directive 2006/42/EC, modified.

- Low voltage directive 2006/95/EC, modified.

- Electromagnetic compatibility directive 2004/108/EC, modified, and the applicable recommendations of European standards.

- Machine safety: electrical equipment in machines, general requirements, EN 60204-1.

- Electromagnetic emission and immunity EN 61800-3 ‘C3’.

Unit shall be manufactured in a facility registered to ISO 9001 Manufacturing Quality Standard and to ISO 14001 Environmental Management System. Unit shall be tested at the factory.

Third-party testing and certification - all performances must be certified by Eurovent and unit safety must be certified by DEKRA.

Exceptional endurance tests

-   Corrosion resistance tests in salt mist in the laboratory.

-    Accelerated ageing test on components that are submitted to continuous operation: compressor piping,

fan supports.

- Transport simulation test in the laboratory on a vibrating table.

- Packaging crash test to ensure that the units are adequately protected against accidental shocks.

DESIGN PERFORMANCE DATA

Performance data certified by Eurovent independent body (mandatory).

- Cooling capacity (kW): ……

- Seasonal energy efficiency in cooling, ESEER (kW/kW) following EN14511:3 2013 : ……

- Evaporator entering/leaving water temperature (°C): …… / ……

- Fluid type: …….

- Fluid flow rate (l/s): ……

- Water heat exchanger pressure drops (kPa): ……

- Outdoor air temperature (°C): ……

- Sound power level at full load (dB(A)): ……

- Refrigerant type: ……….

- Refrigerant charge: …….. kg  (…. kg/kW)

- Dimensions, length x depth x height (mm): …… x …… x ……

- Unit operating weight: ….. kg

UNIT CONSTRUCTION

- Frame shall be of heavy-gage, painted galvanized steel painted in oven-baked polyester powder paint (Beige color).

- Corrosion-resistant casing.

- Easy access to all internal components: simply undo three screws to remove the complete front panel to access the refrigerant piping connections, control box and electrical connections, as well as the compressor and other key parts.

- Specially shaped anchorage feet ensure correct and safe unit fixing to the foundation.

COMPRESSOR

- Low-noise scroll or rotary compressor with low vibration levels.

- The compressor is placed on anti-vibration mountings and maintenance-free.

WATER HEAT EXCHANGER

- Brazed plate heat exchanger, direct expansion.

- Plate exchangers shall be made of AISI 316 L stainless steel, copper brazed types.

- Heat exchangers shall be thermally insulated with closed cell foam type insulation.

- Heat exchanger shall be tested and stamped in accordance with European PED 97/23/EC Code.

AIR HEAT EXCHANGER

- Unit shall be equipped  with vertical coils

- Protection grilles shall protect the heat exchanger against possible shocks.

- Coil shall be air-cooled cupper tube aluminium fins heat exchanger (Cu/Al).

FANS

- Low-noise fans latest-generation made of a composite material providing more quiet by not generating intrusive low-frequency noise.

- The air management system, consisting of the propeller fan, orifice and air discharge grille, guarantees minimized sound levels.

- Rigid fan installation for reduced start-up noise.

REFRIGERANT

- HFC R410-A refrigerant

REFRIGERANT CIRCUIT

Units shall operate with R-410A refrigerant.

The refrigerant circuit shall be leak-tight with:

- Brazed refrigerant connections for increased leaktightness.

- Verification of pressure transducers and temperature sensors without transferring refrigerant charge.

- Thermostatic  expansion valve (TXV)

- High-pressure refrigerant protection.

ELECTRIC FEATURES

- Unit shall operate on 400V, 3-phase, 50 Hz +/-10% power supply with neutral.

- Single power supply point.

- Various power cable outlet options: pre-punched holes in the cabinet panels permit cable exit on the side, front or rear.

ELECTRICAL CHARACTERISTICS

- Single point power connection.

- Unit shall operate on 3-phase power supply at the voltage shown in the equipment schedule.

- Control points shall be accessed through terminal block.

- Unit shall be shipped with factory control and power wiring installed.

CONTROLS

The electronic control system shall combine intelligence with operating simplicity.

The control shall constantly monitor all machine parameters and precisely manage the operation of compressor, expansion devices, fans and the water heat exchanger pump for optimum energy efficiency.

- Energy management

- Seven-day internal time schedule clock shall be available so as to permit unit on/off control and operation at a second set point.

- Set point reset shall be based on the outside air temperature or the return water temperature or on the water heat exchanger delta T.

Master/slave operation

- Two units connected by CCN shall cooperate to assure system water temperature.

- The master unit shall be the only interface to control the operation of both chillers.

- Up to 5 possible water loop configuration (parallel, common or dedicated pumps, series…).

- Three balance modes: Disabled, only on failure, according to run times.

- Common pump management (external pump and units provided with flow switch only) or dedicated pump management (internal pump can be used).

- Unit Start/stop can be based on the outside air temperature.

- Integrated features

- Night mode: Capacity and fan speed limitation for reduced noise level

- An HMI (Aquasnap junior remote controller) graphic service interface can be used to monitor and set the unit operating parameters.

Fast diagnosis of possible incidents and their history via the Pro-Dialog+ control

- Auto-adaptive control

- Control algorithm prevents excessive compressor cycling and permits reduction of the water quantity in the hydronic circuit.

User interfaces

The unit can use the following user interfaces:

-     Dry contacts

-  Remote controller (option)

Remote operating mode with volt-free contacts (standard)

- Start/stop: Opening of this contact will shut down the unit

- Dual set point: Closing of this contact activates a second set point (example: unoccupied mode)

- Water pump control (contacts supplied with the hydronic module option): These output control the contactor of one water heat exchanger water pump

- Alarm indication: this volt-free contact indicates the presence of a major fault that has led to the shut-down of one or two refrigerant circuits

- Demand limit: Closing of these contact limits the maximum unit capacity to a predefined values.

- User safety: This contact can be used for any customer safety loop, closing of the contact generates a specific alarm

- Out of service: This signal indicates that the unit is completely out of service

OPERATING CHARACTERISTICS

Unit shall be operating efficiently in extreme temperature conditions, down to -10°C and up to 46°C outside temperature.

WATER CIRCUIT

The unit must be equipped with:

- 1 inch gas MPT water connections.

- 3 bar pressure relief valve

- Water flow switch to ensure that the circuits operate with the correct water flow rate.

- Safety valve (1/2” outlet)

- Automatic valve with air vent

- Temperature sensors.

OPTIONS

The following options can be fitted to the unit, as required.

Hydronic module

The hydronic module shall be integrated in the heat pump chassis without increasing its dimensions and include the following elements:

circulation  water pump variable speed, class A, automatic purge valve, Flow switch, 2 temperature sensors to measure inlet/outlet water temperature, Plug to unblock – remove pump, expansion tank.

Only the power and the water supply and the return piping need to be connected.

Expansion tank

Expansion tank shall be supplied with the hydraulic module to protect closed water systems from excessive pressure.

Anti-corrosion protection heat exchanger

Anticorrosive protection can be apply by special coating material based on polyurethane for high flexibility and in the presence of aluminum to generate heat conductivity and resistance to ultraviolet radiation. The corrosion resistance reaches 10,000 hours (according to ASTM B117 standard). The corrosion protection system complies with the requirements of «Erichsen» tests (DIN 53156) for air conditioning systems and the layer thickness should not exceed 25 micron.

The coating material is sent directly from the factory and is ready for use without further mixing or dilution.

The heat exchanger before and after the protection will be like in the photos below.

New coils			      without protection			with anti-corrosion protection

with anti-corrosion protection