Product specifications in italic shall be considered as key requirements.

SYSTEM DESCRIPTION

Factory assembled, air-cooled liquid chiller utilizing scroll compressors, low sound Greenspeed® variable-speed fans and optional hydronic pump module. The unit shall include all necessary wiring, piping, initial charge of R410A refrigerant, microprocessor controls and user display.

Note: Hydronic pump module shall be available with fixed-speed or Greenspeed® variable-speed driven pump(s).

QUALITY ASSURANCE

Unit shall be rated in accordance with EN14511-3 Standard, latest revision and unit performances shall be certified by independent Eurovent certification body. Unit without independent Eurovent certification shall be excluded.

Unit construction shall comply with European directives:

- Commission regulation (EU) N°2016/2281 with regards to Eco-design requirements for chillers.

- Commission regulation (EU) N°327/2011 implementing Directive 2009/125/EC with regards to Eco-design requirements for industrial fans.

- Commission regulation (EU) N°640/2009 implementing Directive 2009/125/EC with regards to Eco-design requirements for electric motors.

- Commission regulation (EU) N°547/2012 implementing Directive 2009/125/EC with regards to Eco-design requirements for water pumps (Unit equipped with hydronic module option).

- Pressurized equipment directive (PED) 2014/68/EC.

- Machinery directive 2006/42/EC, modified.

- Low voltage directive 2014/35/EC, modified.

- Electromagnetic compatibility directive 2014/30/EC, modified, and the applicable recommendations of European standards.

- Machine safety: electrical equipment in machines, general requirements, EN 60204-1.

- Electromagnetic emission and immunity EN 61800-3.

Unit shall be manufactured in a facility registered to ISO 9001 Manufacturing Quality Standard and to ISO 14001 Environmental Management System. Unit shall be tested at the factory.

DESIGN PERFORMANCE DATA

Performance data certified by Eurovent independent body (mandatory).

- Cooling Capacity (kW): ………..*

- SEER according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  7οC/12oC)

- SEER according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  18οC/23oC)

- SEPR according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  7οC/12oC)

- Refrigerant type: R-410A

- Compressor tyrer: Scroll

- Number of Compressors: ….

- Evaporator Pressure Drop (kPa): ......

- Sound power level at full load (dB(A)): ……

- Sound pressure level 10m 10 μέτρων κατά  ISO 4871 (dB (A)): ……

- Refrigerant amount : ...... .. kg (. ... Kg / kW)

- Dimensions, length x depth x height (mm): …… x …… x ……

- Unit operating weight: ….. kg

*Operating Conditions:

- Cold water inlet / outlet temperature (° C): ……..

- Ambient temperature (° C) in cooling mode: ……..οC DB

The above data shall be mentioned in the selection datasheet of the unit

UNIT CONSTRUCTION

- Frame shall be of heavy-gage, painted galvanized steel painted in oven-baked polyester powder paint (light grey, RAL7035).

- Electrical Cabinet shall be galvanized steel casing painted in oven-baked polyester powder paint (light grey, RAL7035).

COMPRESSOR ASSEMBLY

- Fully hermetic scroll type compressors, each equipped with:

- Two-pole electric motor (Direct on line 400V, 2900rpm at 50Hz) cooled by suction gas and protected by internal temperature sensors.

- Initial oil charge of synthetic polyolester oil

- Integral oil level sight glass.

- Electric crankcase heater to minimize oil dilution and refrigerant migration.

- Electronic over temperature motor protection.

Low noise level and low vibration level shall be guaranteed by:

- Flexible anti-vibration mounts to isolate compressor assembly from unit chassis.

- Suction and discharge piping designed to prevent the transmission of vibrations to the unit chassis.

- Optional acoustic compressor enclosure, easily removable with 1/4 turn fasteners.

COOLER (WATER HEAT EXCHANGER)

- Asymmetric Brazed plate heat exchanger, direct expansion.

- Design shall incorporate of 2 independent direct-expansion refrigerant circuits.

- Plate exchangers shall be made of AISI 316L stainless steel, copper brazed type.

- Exchangers shall be thermally insulated with 19mm closed cell foam type insulation with a maximum K factor of 0.28.

- Shall be equipped with Victaulic-type fluid connections.

- Cooler shall be tested and stamped in accordance with European PED 2014/68/EC Code.

- Cooler pressure drop shall not exceed 45 kPa under Eurovent conditions. Cooler with higher pressure drops shall be excluded.

- Cooler shall be provided with a factory-installed electronic flow switch.

CONDENSER (AIR HEAT EXCHANGER)

- Condenser coils shall be designed to ensure sub-cooling of the liquid refrigerant

- Condenser coils shall be V-shaped with a minimum open angle of 50° to ensure optimum air distribution

- Coils shall be entirely made of aluminium alloy, micro-channels type.

- Coils shall consist of a two-pass arrangement

- Coils shall be leak-tested at 45 bar.

FANS

- All fans on the unit shall controlled by variable frequency drive (with Greenspeed® intelligence) to provide higher part load efficiency and reduced acoustic levels.

- All fans shall be automatically controlled (Greenspeed® intelligence) to achieve higher part load efficiency, winter operation down to -20°C outside air temperature as standard, automatic fans speed adjustment in case of coil fouling, floating  condensing pressure, smooth fan start to increase unit lifetime and eliminate start/stop noise for sensitive acoustic applications.

- Each refrigerant circuit shall have a factory-installed, independent variable frequency drive. Variable speed drives shall be rated IP 55 enclosures and CE compliant.

- Condenser fans shall have a minimum overall efficiency higher than the minimum efficiency target to comply with commission regulation (EU) N°327/2011 implementing Directive 2009/125/EC with regards to Eco-design requirements for industrial fans.

- Condenser fans shall be direct-driven, 9-blade airfoil cross-section, reinforced polymer construction with inherent corrosion resistance, axial type, statically and dynamically balanced.

- Air shall be discharged vertically upward.

- Fans shall be protected by coated steel wire safety guards.

- Winter operation down to -20°C outside air temperature as standard

REFRIGERANT

- HFC R410-A refrigerant

- Total unit refrigerant charge shall not exceed 0.14 kg/kW of cooling capacity at Eurovent conditions. Units with higher refrigerant charge shall be excluded.

REFRIGERATION COMPONENTS

Each refrigerant circuit components shall include:

- Replaceable-core filter drier.

- Moisture indicating sight glass.

- Electronic expansion device.

- Liquid line service valves.

- Complete operating charge of refrigerant R-410A and compressor oil.

ELECTRIC FEATURES

- Unit shall operate on 400V, 3-phase, 50 Hz +/-10% power supply without neutral.

- Control voltage shall be supplied by a factory-installed transformer.

- Unit shall be supplied with factory-installed main circuit breaker, also  acting as electrical disconnect/isolator.

CONTROLS, SAFETIES, AND DIAGNOSTICS

Unit controls shall include the following minimum components:

- Microprocessor with non-volatile memory.

- Power transformer to serve all controllers, relays, and control components.

- LCD user display.

- Remote control by contact or CCN.

- Replaceable controller boards.

- Pressure sensors to measure suction and discharge pressure.

- Thermistors to measure cooler entering and leaving fluid temperatures, outside air temperature and refrigerant suction temperature.

- Programmable flow switch or water pressure transducers to protect against low water flow situation.

Controls features

- Automatic circuit lead/lag.

- Refrigerant parameters control (suction superheat, condensing pressure control).

- Capacity control based on leaving (or entering) chilled fluid temperature and compensated by rate of change of return-fluid temperature.

- Leaving or entering chilled fluid temperature reset from outside air temperature, differential chilled water temperature or via a 0-10V signal.

- Provision of a dual set point for the leaving chilled water temperature activated by a remote contact closure signal or by the built in time clock.

- Chilled fluid temperature pull-down rate at start-up adjustable range from 0.11°C to 1.1°C per minute to prevent excessive demand spikes at start-up.

- Programmable seven-day time schedule. Up to 14 holiday period definitions.

- Night time sound control through demand limit and fan speed control to reduce the sound of the machine by a user-defined schedule.

- Equal run time rotation of compressors and pumps and number of starts

- Demand limit control (configurable from 0% to 100 %) activated by remote contact closure.

- Remote system interlock.

- Alarm and Running outputs.

- Installation, Operation and Maintenance manual, and machine spares part list shall be available in   electronic format and easy accessible by connecting a laptop to the control panel.

- Chilled water pump start/stop control.

- Water flow and external static pressure electronic calculation.

- Electronic setting of the water pump speed and the water flow (unit equipped with variable-speed pump hydronic module).

- Start/Stop command of external water pump (up to 2).

- Variable speed command of one external water loop pump by 0-10 V signal.

- Low ambient protection to energize cooler and hydronic system trace heating (optional).

- Periodic pump start to ensure pump seals are properly maintained during off-season periods.

Pro-Dialog+ User Interface

The control panel shall include, as standard, a user interface that provides:

- Multi-language display capability (English, French, German, Dutch, Italian, Spanish or Portuguese).

- Status reading of all internal values such as pressures and temperatures.

- Current operating mode and control point.

- Water flow and external static pressure electronic readings.

- Unit Configuration.

- On-board time schedule configuration.

- 3 access levels for Standard, User and Service.

- Text-based alarm, diagnostic and alarm history messages.

- Red and green LEDs for easy status check.

User interface shall have back light and contrast adjustment for easy viewing in bright sunlight or night conditions.

Control Diagnostics

Unit control display shall include the following information for fault diagnostics:

- Compressor lockout.

- Protection against loss of charge.

- Low fluid flow.

- Cooler freeze protection.

- Thermistor and transducer malfunction.

- Entering and leaving-fluid temperature.

- Evaporator and condenser refrigerant pressure.

- Chiller starts number and run hours.

- Compressor starts number and run hours.

- Fan starts number and run hours.

- Pump starts number and run hours.

- Quick test shall verify operation of every switch, fan, pump and compressor before chiller is started.

Diagnostics shall include the ability to view the list of the 10 alarms currently active with clear language descriptions of the alarm event.

- 2 alarm history buffers shall allow the user to store no less than 50 alarm events with clear language descriptions, time and date stamp event entry. One alarm history shall be dedicated to general alarms while the other shall only display major failures.

- The control system shall allow software upgrade without the need for new hardware modules.

Safeties

Unit shall be equipped with thermistors / transducers and all other control devices to protect from the following:

- Reverse rotation or wrong electrical power connection.

- Low chilled fluid temperature.

- Thermal overload.

- High Pressure (software control override + pressure switch) made by software to avoid mechanical protection by pressure gauge opening.

- Low suction refrigerant pressure.

- Electrical overload.

- Loss of phase.

- Low voltage power supply failure.

- Low water flow rate.

OPERATING CHARACTERISTICS

Unit shall be capable of starting and running at outdoor ambient temperatures from -20°C to 48°C.

Unit shall be capable of starting up with 40°C entering fluid temperature to the cooler.

ELECTRICAL CHARACTERISTICS

- Unit shall be supplied with main on/off disconnect switch without fuse.

- Single point power connection.

- Unit shall operate on 3-phase power at the voltage shown in the equipment schedule.

- Control points shall be accessed through terminal block.

- Unit shall be shipped with factory control and power wiring installed.

CHILLED WATER CIRCUIT

Chilled water circuit shall be rated for 10 bars maximum working pressure.

OPTIONS

The following options can be fitted to the unit, as required.

Hydronic module

- The hydronic module shall be integrated in the chiller chassis without increasing its dimensions and include the following elements: easily removable strainer, water pump with three-phase motor, accurate and reliable electronic water flow control (flow switch with paddle shall not be accepted), safety relief valve. Water flow and external static pressure electronic readings shall be available through operator user interface. Additional pressure/temperature taps (2) shall be factory installed to measure the pressure differential across the hydronic module.

- Water pump shall comply with Commission regulation (EU) N°547/2012 implementing Directive 2009/125/EC with regards to Eco-design requirements.

- Pump motors shall be totally enclosed single speed, 3-phase type with permanently lubricated bearings, Class F insulation. Pump motors shall be IE2 efficiency level rated.

- Each pump shall be 100% factory tested per Hydraulic Standards.

- The pump shall be protected against cavitation through electronic pressure control at pump inlet.

- Pump casing shall be of cast iron with cataphoresis coating.

- The impeller shall be of AISI 316L stainless steel laser technology welded.

- A choice of 6 hydronic modules shall be available:

- High-pressure single-pump hydronic module.

- High-pressure dual-pump hydronic module.

- Low-pressure single-pump hydronic module.

- Low-pressure dual-pump hydronic module.

- High-pressure variable-speed single-pump hydronic module.

- High-pressure variable-speed dual-pump hydronic module.

- Dual pump hydronic module shall have two independent electric motors and two independent impellers to ensure reliable operation.

- Cast iron body strainer with 1.2 mm mesh screen.

- The water piping shall be protected against corrosion and equipped with drain and vent plugs.

- The piping and the water pump shall be fully insulated to prevent condensation (pump insulation using polyurethane foam and painted steel casing).

- Frost protection down to -20°C shall be guaranteed by optional electric trace-heating  (24 volt) and the water pump shall be automatically started by the controller safety logic in case of a risk of frost formation.

- The customer connections shall be Victaulic connections.

Additional specifications for variable-speed pump hydronic module

- Hydronic module with variable-speed single pump shall be equipped with one VFD (variable frequency drive) to save energy.

- Hydronic module with variable-speed dual pump shall be equipped with two VFDs (variable frequency drive) for full redundancy and to save energy.

- VFD drive along with Greenspeed® intelligence shall be able to vary the pump motor speed in the 30-50 Hz frequency range.

- Nominal unit water flow shall be established through electronic setting of the pump speed to achieve energy savings. Use of a regulating valve to set nominal water flow shall not be accepted.

- Water flow control based on compressor usage, constant system pressure difference or constant system temperature difference shall be available on choice.

Partial heat reclaim

Unit equipped with one desuperheater on each refrigerant circuit for production of free high-temperature hot-water simultaneously with chilled or hot water production. Consist of one BPHE per refrigerant circuit to recover approximately 20% of the rejected heat for the production of hot water up to +65oC.

The unit shall operate in two modes:

- Efficiency priority mode

In this mode unit control optimises unit efficiency. Heat reclaim is based on the saturated condensing temperature. The percentage of the reclaimed heating capacity compared with the total capacity rejected by the condenser increases in proportion to the saturated condensing temperature. This temperature is directly linked to the condenser entering air temperature.

- Reclaim priority mode

This configuration allows constant hot water leaving temperature regardless the unit operates at full or partial load. A setpoint is defined that is relative to the minimum condensing temperature to increase the heating capacity reclaimed at the desuperheaters

Evaporator frost protection

Trace heating provides protection against cooler, water piping freezing down to –20°C outside air temperature.

Evaporator and hydronic module frost protection

Trace heating provides protection against cooler, water piping and hydronic module freezing between 0°C and -20°C outside air temperature.

Expansion tank

Expansion tank shall be supplied with the hydraulic module to protect closed water systems from excessive pressure.

Welded evaporator water connection kit

Victaulic connection adapter for easy water piping connection.

Low noise level

Aesthetic and sound absorbing compressor enclosure to reduce noise level by 1 to 2 dB(A).

Very low noise level

Aesthetic and sound absorbing compressor enclosure associated with low-speed fans to reduce noise level by 6 to 7 dB(A).

Brine options (Not compatible with MCHE coils)

Brine option for LWT from +5oC to 0°C

This option allows production for LWT  from +5oC to 0°C

Brine option for LWT from 0oC to -15°C

This option allows production for LWT  from 0oC to -12°C with propylene glycol (max. 45%) or from 0oC to -15°C with ethylene glycol (max. 45%).

Compressor discharge valves

Shut-off valves on the compressor suction and discharge piping	 for simplified maintenance (Possibility to store the refrigerant charge in the cooler or condenser side during servicing).

Compressor suction and discharge valves

Shut-off valves on the compressor discharge piping for simplified maintenance (Possibility to store the refrigerant charge in the condenser side during servicing).

Enclosure panels

Side enclosure panels at each end of the coil to improve aesthetics, to protect coil and piping against impacts.

Grilles and enclosure panels

Metal grilles on the 4 unit sides, plus side enclosure panels at each end of the coil to protect against intrusion to the unit interior, to improve aesthetics while protecting coil and piping protection against impacts.

Enviro-Shield® anti-corrosion protection

- Coils shall be suitable for installations in moderately corrosive environment. The protection shall consist on a nano-scale conversion coating, 100 to 200 nm thick, which uniformly covers the entire surface of the coil. Non conversion coating shall not be accepted. The coating process shall include immersion in a coating bath. The coating shall be applied by an autocatalytic conversion process which shall modify the surface of the aluminum producing a coating that is integral to the coil. Complete immersion shall ensure that 100% of the surface is coated, forming a continuous and even film. Spray coating process shall not be accepted. The coating shall be integral to the MCHE and shall not flake or loose adhesion with cross hatch adhesion of 5B per ASTM D3359. The thin coating shall have no variation in heat transfer on air flow per ARI 410. The coating shall utilise corrosion inhibitors which actively arrest damage due to environmental or mechanical damage. Corrosion durability of coated microchannel coils shall be confirmed through testing to no less than 4000 hours constant neutral salt spray per ASTM B117.

Super Enviro-Shield® anti-corrosion protection

- Coils shall be suitable for installations in the most severe environments. The protection shall consist on a flexible epoxy polymer coating uniformly applied to all coil external surface areas without material bridging between fins and louvers. The coating process shall be an electrocoating process with immersion in a coating bath and a final UV protective topcoat to shield the fins from ultraviolet degradation and to ensure coating durability and long life. Spray coating and non-electrocoating shall not be accepted. Coating process shall ensure complete coil encapsulation, including all exposed fin edges. The coating shall have a uniform thickness of 20 to 40 μm on all external coil surface areas including fin edges. The coating shall have minimal variation (<1%) in heat transfer on air flow per ARI 410. The coating shall have superior hardness characteristics of 2H per ASTM D3363 and cross hatch adhesion of 4B-5B per ASTM D3359. Impact resistance shall be up yo 100 in/lb (ASTM D2794). Corrosion durability of coated microchannel coils shall be confirmed through testing to no less than 6000 hours constant neutral salt spray per ASTM B117.

Soft starter

Electronic starter on each compressor to reduce the start-up current.

Master/slave operation

- Two units connected by CCN shall cooperate to assure system water temperature.

- The master unit shall be the only interface to control the operation of both chillers.

- Up to 5 possible water loop configuration (parallel, common or dedicated pumps, series…).

- Three balance modes: Disabled, only on failure, according to run times.

- Common pump management (external pump and units provided with flow switch only) or dedicated pump management (internal pump can be used).

Energy management module

Communication board with additional inputs/outputs

Input contacts:

Set-point reset by indoor air temperature sensor (10 kOhms) or by a 4 to 20 mA signal.

Time schedule override.

End of ice production (ice storage).

One additional demand limit volt-free input.

Demand limitation by 0-10 V signal.

- -	Output contacts:

Instantaneous chiller capacity by 0-10 V signal.

Alert indicator.

Complete shut-down due to a chiller fault.

Boiler on/off command during winter season (heat mode by changeover or manual configuration).

CCN to J-Bus gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a JBUS Local Area Network (JBUS, ModBUS). Field programming for customisation is possible.

CCN to Lon gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a LonWorks® Local Area Network (LON, i.e., LonWorks FT-10A ANSI/ EIA-709.1). Field programming shall be required.

Electrical Plug

- 230V/0.8A AC power supply source provided with plug socket for connections of laptops.

TOUCH PILOT CONTROL

The Touch Pilot Control includes advanced communication technology over Ethernet (IP), user-friendly and intuitive user interface with 5" color touch screen.

Advanced Controls Features

- Web connectivity

- Fast BACnet IP connectivity (with “BACnet® IP Communication” option).

- Wireless IP connectivity (with “Carrier Connect” option – for control of the system from the Carrier maintenance department).

- Energy monitoring and trending capabilities (with “Electric energy meter” option).

- Alarm notification through emails.

- Trending capability (display by Web Browser only).

Touch Pilot, 5” User Interface

- Modern and intuitive 5 inch color screen.

- Finger or pencil touch capable.

- All local interaction accessible (Quick test, Start/Stop, Operating mode, …).

- Trending display.

- Synoptic screen with current operating status and physical values.

- 8 unicode languages supported including Chinese.

- Possibility to load a custom translation file.

- Access to the interface through Web Browser.

- Capacity to add up to two (2) user e-mail addresses for the automatic submission of fault reports.

BACnet/IP gateway (compatibility with Touch Pilot Control only)

Unit shall be supplied with factory-installed two-directional high-speed communication using BACnet protocol over Ethernet network (IP). This option shall allow unit integration with BACnet building automation system using Internet Protocol.  This new generation of BACnet IP communication shall allow high speed communications with building management systems, no limitation in reading/writing controller points and shall use standardized alarm codes as defined with BACnet protocol. Field programming may be required.