Product specifications in italic shall be considered as key requirements.

SYSTEM DESCRIPTION

Factory assembled, air to water chiller utilizing scroll compressors, fixed-speed fans and optional hydronic pump module. The unit shall include all necessary wiring, piping, charge of R410A refrigerant, microprocessor controls and user display.

Note: Hydronic pump module shall be available with fixed-speed or variable-speed driven pump(s) and include all the necessary components as described in hydronic module option.

QUALITY ASSURANCE

Unit shall be rated in accordance with EN14511-3 Standard, latest revision and unit performances shall be certified by independent Eurovent certification body. Unit without independent Eurovent certification shall be excluded.

Unit construction shall comply with European directives:

- Commission regulation (EU) N°2016/2281 with regards to Eco-design requirements for chillers.

- Commission regulation (EU) N°327/2011 implementing Directive 2009/125/EC with regards to Eco-design requirements for industrial fans.

- Commission regulation (EU) N°640/2009 implementing Directive 2009/125/EC with regards to Eco-design requirements for electric motors.

- Pressurized equipment directive (PED) 2014/68/EC.

- Machinery directive 2006/42/EC, modified.

- Electromagnetic compatibility directive 2014/30/EC, modified, and the applicable recommendations of European standards.

- Machine safety: electrical equipment in machines, general requirements, EN 60204-1.

Unit shall be manufactured in a facility registered to ISO 9001 Manufacturing Quality Standard and to ISO 14001 Environmental Management System. Unit shall be tested at the factory.

DESIGN PERFORMANCE DATA

- Cooling Capacity (kW): ………..*

- SEER according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  7οC/12oC)

- SEER according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  18οC/23oC)

- SEPR according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  7οC/12oC)

- Refrigerant type: R-410A

- Compressor tyrer: Scroll

- Number of Compressors: ….

- Evaporator Pressure Drop (kPa): ......

- Sound power level at full load (dB(A)): ……

- Sound pressure level 10m 10 μέτρων κατά  ISO 4871 (dB (A)): ……

- Refrigerant amount : ...... .. kg (. ... Kg / kW)

- Dimensions, length x depth x height (mm): …… x …… x ……

- Unit operating weight: ….. kg

*Operating Conditions:

- Cold water inlet / outlet temperature (° C): ……..

- Ambient temperature (° C) in cooling mode: ……..οC DB

The above data shall be mentioned in the selection datasheet of the unit.

UNIT CONSTRUCTION

- Frame shall be of heavy-gage, painted galvanized steel painted in oven-baked polyester powder paint (light grey, RAL7035).

- Electrical Cabinet shall be galvanized steel casing painted in oven-baked polyester powder paint (light grey, RAL7035).

COMPRESSOR ASSEMBLY

- Fully hermetic scroll type compressors, each equipped with:

- Two-pole electric motor (Direct on line 400V, 2900rpm at 50Hz) cooled by suction gas and protected by internal temperature sensors.

- Initial oil charge of synthetic polyolester oil.

- Integral oil level sight glass.

- Electric crankcase heater to minimize oil dilution and refrigerant migration.

- Electronic over temperature motor protection.

- Optional soft starter to minimize compressor starting current with phase loss protection.

Low noise level and low vibration level shall be guaranteed by:

- Flexible anti-vibration mounts to isolate compressor assembly from unit chassis.

- Suction and discharge piping designed to prevent the transmission of vibrations to the unit chassis.

Optional acoustic compressor jacket.

WATER HEAT EXCHANGER

- Brazed plate heat exchanger, direct expansion.

- For sizes over than 130kWatts,design shall incorporate a minimum of 2 independent direct-expansion refrigerant circuits connected in one water circuit.

- Plate exchangers shall be made of AISI 316 L stainless steel, copper brazed types.

- Heat exchangers shall be thermally insulated with 19mm closed cell foam type insulation.

- Shall be equipped with Victaulic-type fluid connections.

- Heat exchanger shall be tested and stamped in accordance with European PED 97/23/EC Code.

AIR HEAT EXCHANGER

- Vertical condenser coils

- Coil shall be air-cooled micro-channel heat exchanger (MCHE), entirely made of aluminium fins.

- Aluminium fins significantly increase the corrosion resistance by eliminating the galvanic currents that are created when two different metals (copper and aluminium) come into contact in traditional heat exchangers.

- Furthermore, the Enviro-Shield and Super Enviro-Shield anti-corrosion protections shall be applied to increase the application range of the MCHE coil from medium to very corrosive environments.

- Coil shall have a series of flat tubes containing a series of multiple, parallel flow micro channels layered between the refrigerant manifolds.

- Coils shall consist of a two pass arrangement.

- Assembled air heat exchanger coils shall be 100% leak tested and pressure tested at 45 bars.

FANS

- Low-noise latest-generation Flying Bird IV fans, made of a composite material providing more quiet by not generating intrusive low-frequency noise, controlled by a variable-frequency controller (factory installed) to provide up to 240 Pa available pressure (depending on the size) at nominal flow rate

- Rigid fan installation for reduced start-up noise.

- Flow control in accordance with the ducting for optimised efficiency with the possibility to program a maximum supply air flow.

- Factory installed supply air duct connection frame.

- Factory installed suction air connection frame standard for sizes 30RBSY 039-080

- Factory installed suction air filters optional (30RBSY 039-080 only)

REFRIGERANT

- HFC R410-A refrigerant

REFRIGERANT CIRCUIT

- The refrigerant circuit shall include several compressors connected in parallel. At part load, around 99% of the operating time, only the compressors that are absolutely necessary operate. At these conditions the compressors operating are more energy efficient, as they use the total condenser and evaporator capacity.

- The electronic expansion device (EXV) allows operation at a lower condensing pressure (EER, COP and ESEER optimisation).

- Dynamic superheat management for better utilisation of the water heat exchanger surface.

ELECTRIC FEATURES

- Unit shall operate on 400V, 3-phase, 50 Hz +/-10% power supply without neutral.

- Control voltage shall be supplied by a factory-installed transformer.

- Unit shall be supplied with factory-installed main circuit breaker, also  acting as electrical disconnect/isolator.

TOUCH PILOT CONTROL

The Touch Pilot Control shall include advanced communication technology over Ethernet (IP), user-friendly and intuitive user interface with 4.3" colour touch screen shall provide the following features.

- Energy management

- Internal time schedule clock: Controls heat pump on/off times and operation at a second set-point

- Set-point offset based on the outside air temperature

- Master/slave control of two heat pumps operating in parallel with operating time equalisation and automatic change-over in case of a unit fault.

- Integrated advanced communication features

- Night mode: Capacity and fan speed limitation for reduced noise level

- For units with hydraulic module: Water pressure display and water flow rate calculation

- Easy and high-speed communication technology over Ethernet (IP) to a building management system

- Access to multiple unit parameters.

- For units without hydraulic module: 0-10V output shall be available for external variable speed pump controL

- 4.3’’ Touch Pilot user interface

- Intuitive and user-friendly 4.3 inch touch screen interface

- Concise and clear information shall be available in 6 languages (English, Spanish, French, German, Italian and a possibility to add a sixth one based on user’s preference)

- Complete menu, customised for different users (end user, service personnel or engineers).

- Capacity to add up to two (2) user e-mail addresses for the automatic submission of fault reports.

Remote management

Unit shall can be easily accessed with Touch Pilot control from the internet, using a PC with an Ethernet connection. This makes remote control quick and easy and offers significant advantages for service operations.

The unit shall be equipped with an RS485 serial port that offers multiple remote control, monitoring and diagnostic possibilities. The unit shall be also communicate with other building management systems via optional communication gateways.

A connection terminal allows remote control of the unit by wired cable as follows:

- Start/stop: Opening of this contact will shut down the unit

- Dual set-point: Closing of this contact activates a second set-point (example: unoccupied mode).

- Demand limit: Closing of this contact limits the maximum chiller capacity to a predefined value.

- Operation indication: This volt-free contact indicates that the chiller is operating (cooling load).

- Alarm indication: This volt-free contact indicates the presence of a major fault that has led to the shut-down of one or several refrigerant circuits.

OPERATING CHARACTERISTICS

Unit shall be capable of starting and running at full or partial load as follows:

In cooling mode at outdoor ambient temperatures from -10°C to 48°C as standard.

ELECTRICAL CHARACTERISTICS

- Unit shall be supplied with main on/off disconnect switch without fuse.

- Single point power connection.

- Unit shall operate on 3-phase power supply at the voltage shown in the equipment schedule.

- Control points shall be accessed through terminal block.

- Unit shall be shipped with factory control and power wiring installed.

WATER CIRCUIT

Water circuit shall be rated for 10 bars maximum working pressure.

OPTIONS

The following options can be fitted to the unit, as required.

Brine options

Brine option for LWT from +5oC to 0°C

This option allows production for LWT  from +5oC to 0°C

Brine option for LWT from 0oC to -15°C

This option allows production for LWT  from 0oC to -12°C with propylene glycol (max. 45%) or from 0oC to -15°C with ethylene glycol (max. 45%).

Low sound level operation

Sound reduction from 1 to 6 dB(A) depending on the unit size and consists of 25mm thickness compressor jacket (all sizes) and 700 rpm fans (for sizes 060/070/078/140/160)

Compressor soft starter

Electronic starter on each compressor to reduce the start-up current.

Inlet filter

Factory mounted washable filter at the inlet (for sizes 30RBSY039-080). Efficiency according to EN 779 = G2

Anti-freeze protection down to -20oC outdoor air temperature

The frost protection of the heat pump water piping is guaranteed down to -20oC by automatically energized heaters and pump cycling. Heater for anti-freeze protection shall operate under 24V / 50W or 63W, supplied from the electrical panel of the unit.

Partial heat reclaim

Unit equipped with one desuperheater on each refrigerant circuit for production of free high-temperature hot-water simultaneously with chilled or hot water production. Consist of one BPHE per refrigerant circuit to recover approximately 20% of the rejected heat for the production of hot water up to +65oC.

Master/slave operation

- Two units connected by CCN shall cooperate to assure system water temperature.

- System’s water temperature shall be controlled either by outlet or inlet temperature

- The master unit shall be the only interface to control the operation of both chillers.

- Three balance modes: Disabled, only on failure, according to run times.

Hydronic module

- The hydronic module shall be integrated in the heat pump chassis without increasing its dimensions and include the following elements: easily removable strainer, water pump, pressure relief valve, air purge, 2 drain valves, 2 pressure transducers to measure inlet/outlet pressure, 2 temperature probes to measure inlet/outlet water temperature.  The pump shall be protected against cavitation through electronic pressure control at pump inlet.

- A choice of 4 hydronic modules shall be available:

- High-pressure, fixed-speed, single-pump hydronic module.

- High-pressure, fixed-speed, dual-pump hydronic module.

- High-pressure, variable-speed, single-pump hydronic module.

- High-pressure, variable-speed, dual-pump hydronic module.

Additional specifications for variable-speed pump hydronic module

The hydronic module shall include pressure transducers that permit intelligent measurement of the water flow rate and real-time display on the user interface. All adjustments shall be made directly on the interface, speeding up start-up and maintenance.

Operating logic

Full-load set point

The flow rate control at full load uses the user interface, reducing the pump speed.

Operating mode at part load

Two part-load operating modes shall be included:

- Constant outlet pressure control

The control shall continuously act on the pump speed to ensure a constant outlet pressure.

- Constant delta T control.

The Variable Water Flow algorithm shall maintain a constant delta T no matter what the unit load, reducing the flow rate to the minimum.

Expansion tank

Expansion tank shall be supplied with the hydraulic module to protect closed water systems from excessive pressure.

Anti-corrosion protection with "BLYGOLD POLUAL" treatment for Cu/Al coil only

(not compatible with MCHE coil)

Coating with aluminium hydroxide on finned area, headers and manifold, provided improved resistance in marine, urban, heavy industrial or rural applications.

Anti-corrosion protection with pre-coated gold fins for Cu/Al coil only

(not compatible with MCHE coil)

Fins made of pre-treated aluminium (polyurethane and epoxy) for improved corrosion resistance, recommended for moderate marine and urban environments

Enviro-Shield® anti-corrosion protection

Coils shall be suitable for installations in moderately corrosive environment. The protection shall consist on a nano-scale conversion coating, 100 to 200 nm thick, which uniformly covers the entire surface of the coil. Non conversion coating shall not be accepted. The coating process shall include immersion in a coating bath. The coating shall be applied by an autocatalytic conversion process which shall modify the surface of the aluminum producing a coating that is integral to the coil. Complete immersion shall ensure that 100% of the surface is coated, forming a continuous and even film. Spray coating process shall not be accepted. The coating shall be integral to the MCHE and shall not flake or loose adhesion with cross hatch adhesion of 5B per ASTM D3359. The thin coating shall have no variation in heat transfer on air flow per ARI 410. The coating shall utilise corrosion inhibitors which actively arrest damage due to environmental or mechanical damage. Corrosion durability of coated microchannel coils shall be confirmed through testing to no less than 4000 hours constant neutral salt spray per ASTM B117.

Super Enviro-Shield® anti-corrosion protection

Coils shall be suitable for installations in the most severe environments. The protection shall consist on a flexible epoxy polymer coating uniformly applied to all coil external surface areas without material bridging between fins and louvers. The coating process shall be an electrocoating process with immersion in a coating bath and a final UV protective topcoat to shield the fins from ultraviolet degradation and to ensure coating durability and long life. Spray coating and non-electrocoating shall not be accepted. Coating process shall ensure complete coil encapsulation, including all exposed fin edges. The coating shall have a uniform thickness of 20 to 40 μm on all external coil surface areas including fin edges. The coating shall have minimal variation (<1%) in heat transfer on air flow per ARI 410. The coating shall have superior hardness characteristics of 2H per ASTM D3363 and cross hatch adhesion of 4B-5B per ASTM D3359. Impact resistance shall be up yo 100 in/lb (ASTM D2794). Corrosion durability of coated microchannel coils shall be confirmed through testing to no less than 6000 hours constant neutral salt spray per ASTM B117.

CCN to J-Bus gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a JBUS Local Area Network (JBUS, ModBUS). Field programming for customisation is possible.

CCN to Lon gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a LonWorks® Local Area Network (LON, i.e., LonWorks FT-10A ANSI/ EIA-709.1). Field programming shall be required.

BACnet

Unit shall be supplied with factory-installed two-directional high-speed communication using BACnet protocol.

Reinforced ECM filtration for fan VFD

Fan variable frequency drive compliance to IEC 61800-3 C1 class

Reinforced ECM filtration for pump VFD

Pump variable frequency drive compliance to IEC 61800-3 C1 class.

Set point adjustment by 4-20mA signal.

Connections to allow a 4-20mA signal input.