Product specifications in italic shall be considered as key requirements.

SYSTEM DESCRIPTION

Factory assembled, air to water monoblock chiller utilizing DC inverter Twin-Rotary compressor with Pulse Amplitude Modulation (PAM) and Pulse Width Modulation (PWM) , variable speed fans and optional hydronic pump module. The unit shall include all necessary wiring, piping, charge of R410A refrigerant, microprocessor controls and user display.

Note: Hydronic pump module shall be available with fixed-speed or variable-speed circulator and include all the necessary components as described in hydronic module option.

QUALITY ASSURANCE

Unit shall be rated in accordance with EN14511-3 Standard, latest revision and unit performances shall be certified by independent Eurovent certification body. Unit without independent Eurovent certification shall be excluded.

Unit construction shall comply with European directives:

- Commission regulation (EU) N°2016/2281 with regards to Eco-design requirements for chillers.

- Commission regulation (EU) N°327/2011 implementing Directive 2009/125/EC with regards to Eco-design requirements for industrial fans.

- Commission regulation (EU) N°640/2009 implementing Directive 2009/125/EC with regards to Eco-design requirements for electric motors.

- From 1st January 2015, commission regulation (EU) N°547/2012 implementing Directive 2009/125/EC with regards to Eco-design requirements for water pumps (Unit equipped with hydronic module option).

- Pressurized equipment directive (PED) 97/23/EC.

- Machinery directive 2006/42/EC, modified.

- 60335-2-40

- Electromagnetic compatibility directive 2004/108/EC, modified, and the applicable recommendations of European standards.

- 2011/65/EU (RoHS)

- EN ISO 13857

- EN 62233

Unit shall be manufactured in European country in a facility registered to ISO 9001 Manufacturing Quality Standard and to ISO 14001 Environmental Management System.

Unit shall be tested at the factory.

DESIGN PERFORMANCE DATA

Performance data certified by Eurovent independent body (mandatory).

- Cooling capacity (kW): ……

- Seasonal energy efficiency in cooling, ESEER (kW/kW): ……

- Refrigerant type: R-410A

- Compressor tyrer: DC inverter Twin-Rotary

- Evaporator Pressure Drop (kPa): ......

- Sound power level at full load (dB(A)): ……

- Sound pressure level 10m according to  ISO 4871 (dB (A)): ……

- Refrigerant amount : ...... .. kg (. ... Kg / kW)

- Dimensions, length x depth x height (mm): …… x …… x ……

- Unit operating weight: ….. kg

*Operating Conditions:

- Cold water inlet / outlet temperature (° C): ……..

- Ambient temperature (° C) in cooling mode: ……..οC DB

The above data shall be mentioned in the selection datasheet of the unit.

UNIT CONSTRUCTION

The unit shall have exceptional small foot-print and reduced operating weight. All components shall be enclosed by easily removable panels. The frame of the unit shall be painted in neutral colour RAL 7035.

COMPRESSOR ASSEMBLY

The unit shall be equipped with DC inverter Twin-Rotary compressor. Advanced technology DC inverter twin-rotary compressor shall provide maximum energy-efficiency with high capacity available at peak conditions and optimised efficiency at low and mid compressor speeds. The heat pump DC inverter system shall use Intelligent Power Drive Unit (IPDU) hybrid inverter technology, combining two electronic management logics: Pulse Amplitude Modulation (PAM) and Pulse Width Modulation (PWM) for optimised compressor operation in all conditions, minimised temperature fluctuations, and providing perfect individual comfort control with significantly reduced energy consumption:

- PAM: pulse amplitude modulation of the direct current shall control the compressor at maximum load conditions (start-up and peak load), increasing the voltage at fixed frequency. The compressor shall work at high speed to rapidly achieve the desired temperature.

- PWM: pulse width modulation of the direct current shall control the compressor at partial load conditions, adjusting the frequency at fixed voltage. The compressor speed shall be fine-tuned and the system shall provide high-level comfort (no temperature fluctuations) at exceptionally efficient working conditions.

The pulse modulation valve shall be a bi-flow electronic expansion device which optimizes the refrigerant amount in the circuit and the superheat, preventing refrigerant migration back into the compressor. This device shall further enhance high system performance and reliability.

Compressor frequency shall be increased continuously up to the maximum level. This shall ensure that there are no current draw peaks in the start-up phase and safe connection to a single phase power supply even in large-capacity systems (for single power connection units).

The two rotary compression cylinders, shall offset from each other by 180°, and the DC brushless motor  with the shaft in perfect balance shall ensure reduced vibration and noise, even at very low operating speeds. This shall obtain an extremely wide range between minimum and maximum capacity with continuous operation, guaranteeing that the system shall be always optimised and shall provide maximum comfort at exceptionally high efficiency levels. Twin-rotary cylinders, low vibrations and low load to the shaft shall ensure highest compressor reliability and a long trouble-free operating life.

All DC brushless twin-rotary compressors shall be equipped with crankcase heaters as standard.

A standard double compressor shield for acoustic insulation further shall reduce noise levels.

The compressor sub-assembly shall be completed with:

- Anti-vibration mountings between the unit and the compressor chassis.

- A high-pressure switch or compressor case thermostat control at the discharge of compressor.

WATER HEAT EXCHANGER

The unit shall be equipped with high efficiency brazed plate heat exchanger, made of AISI 316L stainless steel.

AIR HEAT EXCHANGER

The unit shall be equipped with vertical condenser coils. Heat exchanger shall be air-cooled with internally grooved copper tube aluminium fins (Cu/Al).

FANS

The unit shall be equipped with Brushless DC motor for increased fan performance and reliability and with variable speed fan(s) made of composite materials with an innovative patented fan blade shape to ensure improved air distribution at exceptionally low noise levels . The fans shall be driven by permanent magnet synchronous motor.

REFRIGERANT

The unit shall work  with R410A refrigerant

REFRIGERANT CIRCUIT

The unit shall have electronic system management with several sensors placed in key positions in the refrigerant circuit electronically detect the operational system status. Two micro-controllers shall receive the input from the sensors, manage them using advanced control algorithms and optimize the refrigerant flow and the functioning of all core components - the compressor, fan motors and the pulse modulation valve.

The pulse modulation valve shall be an expansion device which optimizes the refrigerant amount in the circuit and the superheat, preventing refrigerant migration back into the compressor. This device shall further enhance high system performance and reliability.

Each pulse modulation valve shall be equipped with a stepper motor (0-500 pulses). Size 17KW shall be equipped with one PMV in its refrigerant circuit, while size 21ΚW shall be equipped with two PMV in its refrigerant circuit in parallel.

Refrigerant circuit shall be equipped with 4 port valve for reversible operation in heating and cooling mode.

OPERATING CHARACTERISTICS

Unit shall be capable to operate at ambient temperatures from -10°C to 46°C.

ELECTRIC FEATURES

The unit shall operate on 400V, 3-phase, 50Hz +/-10%.

The unit shall be equipped with transformer for safe 24V control circuit supply.

CONTROL PANEL – USER INTERFACE

NHC Control shall associate with compressor and fan variable frequency driver combining intelligence with operating simplicity. The control shall constantly monitors all machine parameters and precisely manages the operation of compressor, expansion devices, fans and of the water heat exchanger water pump for optimum energy efficiency.

NHC control shall be associated with the User interface which shall allow easy access to the configuration  parameters (frequency compressor, refrigerant circuit temperature, set points, air temp, entering water temp, alarm report).

The user interface shall also be intuitive in its use. It shall allow reading and easy selection of the operating mode. The functions shall be represented by icons on the LCD backlit screen.

To facilitate the use of the interface, 3 levels of access shall be available: end user, installer and factory.

The following key features shall be available:

-- Master/slave control of 4 units operating in parallel with operating time equalisation and automatic changeover in case of a unit fault .

The following 3 choices for unit’s control shall be available:

The unit shall alternatively be driven through

    - Dry contact

    - User interface

    - ModBus protocol

The interface shall have the possibility to be installed up to 50 m away from the unit. It shall be connected to the main control board with a 4 wires cable.

The interface shall provide 2 installation possibilities:

Inside the room (with remote interface accessory) : Remote interface shall have an internal sensor to measure the room temperature.

On the unit (with local user interface option) : Setpoint of the water temperature shall be controlled.

- ModBus:

The control board shall have direct access with Modbus connection to set, configure and monitor the unit.

- Input remote contacts:

The unit shall provide the following remote contacts.

- Remote On/Off Contact

- Remote Economic Contact: This switch shall be used to select the regular Home Mode or the Economic Away Mode when contact is closed. For Home Mode the contact shall be opened and for Economic Away mode the contact shall be closed.

- Safety Input Contact: This switch shall be normally closed type, according to configuration it shall be used either to stop the unit, or to ban the Cooling Mode when contact is opened.

- Large choice of Input Contacts

Several functions shall be configured by the installer. They shall allow to adapt to the environment of the unit. The unit shall have the below contacts and configurations:

- Power Limitation / Night Mode: This switch shall be used to reduce the compressor maximum frequency to avoid noise.

- Off Peak (General Purpose Contact 1): If this General Purpose Contact, configured to “Off Peak”, is closed then the Electric Heat Stages shall not allowed.

- Loadshed Request (General Purpose Contact 2): If this General Purpose Contact, configured to “Loadshed Request”, is closed then unit shall be stopped as soon as possible.

- Energy Meter Input : This input shall be used to count the number of pulses received from an external energy meter (not supplied)

- External Alarm Indication Input : When this input is opened, alarm shall be tripped. This alarm shall be for information only, without affecting the unit operation.

- Output remote contact available

Two output contacts shall be available on the unit’s control board, offering the following purposes upon configuration:

- alert,

- alarm,

- Standby,

- running,

- indoor air temperature reached,

HYDRONIC MODULE

For added flexibility units shall be available with or without an integrated hydronic module, to suit the installation. The hydronic module shall be integrated into the unit without increasing its dimensions and saves the space normally used for the water pump. The water heat exchanger and the hydronic module shall be protected against frost down to -20°C, using an electric resistance heater (standard) and pump cycling.

2 Hydronics modules shall be available in option :

- With fixed speed pump

- With Variable speed circulator.

- Units with hydraulic module shall include the following elements:

- Mesh filter

- Water drain valve

- Paddle flow switch

- Expansion tank

- Safety valve

- Water Pump (either fixed-speed or inverter)

- Temperature sensor

- Anti-freeze electric heater

MAIN FEATURES

The following features shall be available and factory installed as part of the unit’s control algorithm or and user’s interface configuration:

- The unit shall control an additional water pump

- Up to 4 units connected in master/slave mode, with operating time equalisation and automatic changeover in case of a unit fault, controlled by the master unit and with one common user interface. The operating logic of the units shall be either in parallel or in cascade logic. In case of cascade logic, the following configurations shall be available:

- Starting Master First, then first Slave to last Slave. Stopping Last Slave to first Slave, then Master.

- Starting/stopping units according to their wear factors.

- All units (Master and Slaves) shall be started/stopped at the same time.

- The user interface offer the choice to select between 2 compensation curves, or tο set a new customised compensation curve.