Product specifications in italic shall be considered as key requirements.

SYSTEM DESCRIPTION

Factory assembled, air to water heat pump utilizing scroll compressor, fixed-speed fans and optional hydronic pump module. The unit shall include all necessary wiring, piping, charge of R410A refrigerant, microprocessor controls and user display.

Note: Hydronic pump module shall be available with a single-speed circulator Class A and include all the necessary components as described in hydronic module option.

QUALITY ASSURANCE

Unit shall be rated in accordance with EN14511-3 Standard, latest revision and unit performances shall be certified by independent Eurovent certification body. Unit without independent Eurovent certification shall be excluded.

Unit construction shall comply with European directives:

- Commission Regulation (EU) N° 813/2013 implementing Directive 2009/125/EC of the European Parliament and of the Council with regard to Eco-design requirements for space heaters and combination heaters

- Commission regulation (EU) N°327/2011 implementing Directive 2009/125/EC with regards to Eco-design requirements for industrial fans.

- Commission regulation (EU) N°640/2009 implementing Directive 2009/125/EC with regards to Eco-design requirements for electric motors.

- Commission regulation (EU) N°547/2012 implementing Directive 2009/125/EC with regards to Eco-design requirements for water pumps (Unit equipped with hydronic module option).

- Pressurized equipment directive (PED) 97/23/EC.

- Machinery directive 2006/42/EC, modified.

- 60335-2-40

- Electromagnetic compatibility directive 2004/108/EC, modified, and the applicable recommendations of European standards.

- 2011/65/EU (RoHS)

- EN ISO 13857

- EN 62233

Unit shall be manufactured in a facility registered to ISO 9001 Manufacturing Quality Standard and to ISO 14001 Environmental Management System. Unit shall be tested at the factory.

DESIGN PERFORMANCE DATA

Performance data certified by Eurovent independent body (mandatory).

- Cooling Capacity (kW): ………..*

- Heating Capacity (kW): ………..*

- SCOP according to EN14825: 3 2013 (kWh / kWh): ………..(average climate zone and water temperature  30οC/35oC)

- SEER according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  7οC/12oC)

- SEER according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  18οC/23oC)

- SEPR according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  7οC/12oC)

- Refrigerant type: R-410A

- Compressor type: Scroll

- Number of Compressors: ….

- Evaporator Pressure Drop (kPa): ......

- Sound power level at full load (dB(A)): ……

- Sound pressure level 10m according to  ISO 4871 (dB (A)): ……

- Refrigerant amount : ...... .. kg (. ... Kg / kW)

- Dimensions, length x depth x height (mm): …… x …… x ……

- Unit operating weight: ….. kg

*Operating Conditions:

- Cold water inlet / outlet temperature (° C): ……..

- Hot water inlet / outlet temperature (° C): ……..

- Ambient temperature (° C) in cooling mode: ……..οC DB

- Ambient temperature (° C) in heating mode: ……..οC DB (RH 87%)

The above data shall be mentioned in the selection datasheet of the unit.

UNIT CONSTRUCTION

- Frame shall be of heavy-gage, painted galvanized steel painted in oven-baked polyester powder paint (colour Beige).

COMPRESSOR

- Fully hermetic scroll type compressor, equipped with:

- Two-pole electric motor (Direct on line 400V, 2900rpm at 50Hz) cooled by suction gas and protected by internal temperature sensors.

- Initial oil charge of synthetic polyolester oil.

- Integral oil level sight glass.

- Electric crankcase heater to minimize oil dilution and refrigerant migration.

- Electronic over temperature motor protection.

Low noise level and low vibration level shall be guaranteed by:

- Flexible anti-vibration mounts to isolate compressor assembly from unit chassis.

- Suction and discharge piping designed to prevent the transmission of vibrations to the unit chassis.

WATER HEAT EXCHANGER

- Brazed plate heat exchanger, direct expansion.

- Plate exchangers shall be made of AISI 316 L stainless steel, copper brazed types.

- Heat exchangers shall be thermally insulated with closed cell foam type insulation.

- Heat exchanger shall be tested and stamped in accordance with European PED 97/23/EC Code.

AIR HEAT EXCHANGER

- Unit shall be equipped  with vertical evaporator coils

- Protection grilles shall protect the heat exchanger against possible shocks.

- Coil shall be air-cooled cupper tube aluminium fins heat exchanger (Cu/Al).

FANS

- Low-noise fans, provide more quiet by not generating intrusive low-frequency noise

- Rigid fan installation for reduced start-up noise.

REFRIGERANT

- HFC R410-A refrigerant

REFRIGERANT CIRCUIT

The refrigerant circuit shall include one compressor The electronic expansion device (EXV) allows operation at a lower condensing pressure (ESEER optimisation).

ELECTRIC FEATURES

- Unit shall operate on 400V, 3-phase, 50 Hz +/-10% power supply with neutral cable up to 33 kW and without neutral for 40  kW.

- Control voltage shall be supplied by a factory-installed transformer.

- Unit shall be supplied with factory-installed main circuit breaker, also  acting as electrical disconnect/isolator.

CONTROLS

Control panel shall include an alphanumeric eight-line display, two LEDs and five navigation keys as well as a contrast control wheel. The following features shall be provided by the control panel:

- Energy management

- Seven-day internal time schedule clock: Permits unit on/ off control and operation at a second set point

Master/slave operation

- Two units connected by CCN shall cooperate to assure system water temperature.

- The master unit shall be the only interface to control the operation of both chillers.

- Up to 5 possible water loop configuration (parallel, common or dedicated pumps, series…).

- Three balance modes: Disabled, only on failure, according to run times.

- Common pump management (external pump and units provided with flow switch only) or dedicated pump management (internal pump can be used).

- Integrated features

- Night mode: Capacity and fan speed limitation for reduced noise level

- Ease-of-use

- Backlighted LCD interface with a manual control potentiometer to ensure legibility under any lighting conditions.

- The information can be displayed clearly in English, French, German, Italian and Spanish.

- Controller’s navigation uses intuitive tree-structure menus, similar to the Internet navigators. They are user-friendly and permit quick access to the principal operating parameters: Number of compressors operating, suction/discharge pressure, compressor operating hours, set point, air temperature, entering/ leaving water temperature.

Remote operating mode with volt-free contacts (standard)

- Start/stop: Opening of this contact will shut down the unit

- Dual set point: Closing of this contact activates a second set point (example: unoccupied mode)

- Water pump control (contacts supplied with the hydronic module option): These output control the contactor heat exchanger water pump.

- Alarm indication: this volt-free contact indicates the presence of a major fault that has led to the shut-down of one or two refrigerant circuits

- Demand limit: Closing these contact limits the maximum unit capacity to three predefined value.

- User safety: This contact can be used for any customer safety loop, closing of the contact generates a specific alarm

- Out of service: This signal indicates that the unit is completely out of service

Remote interface (accessory)

Remote interface shall allow access to the same menus as the unit interface and can be installed up to 300 m away. This accessory includes a box that can be mounted inside the building. The power supply is provided via a 220 V/24 V transformer supplied.

OPERATING CHARACTERISTICS

Unit shall be capable of starting and running at full or partial load as follows:

In cooling mode at outdoor ambient temperatures from -10°C to 48°C as standard,

(Operating range with anti-freeze solution and Pro-Dialog configuration.)

In heating mode at outdoor ambient temperatures from -15°C to 40°C as standard.

ELECTRICAL CHARACTERISTICS

- Unit shall be supplied with main on/off disconnect switch without fuse.

- Single point power connection.

- Unit shall operate on 3-phase power supply at the voltage shown in the equipment schedule.

- Control points shall be accessed through terminal block.

- Unit shall be shipped with factory control and power wiring installed.

OPTIONS

Hydronic module

- The hydronic module shall be integrated in the heat pump chassis without increasing its dimensions and include the following elements:

- Screen filter

- Expansion Tank

- Safety valve

- High-pressure pump

- Air purge

- Water drain valve

- Flow sensor

- Plate heat exchanger leaving temperature sensor

- Plate heat exchanger entering temperature sensor

- Heat exchanger frost protection heater

- Pipe frost protection heater

- Shut-off valve (automatic water fill option)

- Pressure reducer (automatic water fill option)

Expansion tank

Expansion tank shall be supplied with the hydraulic module to protect closed water systems from excessive pressure.

CCN to J-Bus gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a JBUS Local Area Network (JBUS, ModBUS). Field programming for customisation is possible.

CCN to Lon gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a LonWorks® Local Area Network (LON, i.e., LonWorks FT-10A ANSI/ EIA-709.1). Field programming shall be required.

CCN to BACnet

Unit shall be supplied with factory-installed two-directional high-speed communication using BACnet protocol.

Anti-corrosion protection heat exchanger

Anticorrosive protection can be apply by special coating material based on polyurethane for high flexibility and in the presence of aluminum to generate heat conductivity and resistance to ultraviolet radiation. The corrosion resistance reaches 10,000 hours (according to ASTM B117 standard). The corrosion protection system complies with the requirements of «Erichsen» tests (DIN 53156) for air conditioning systems and the layer thickness should not exceed 25 micron.

The coating material is sent directly from the factory and is ready for use without further mixing or dilution.

The heat exchanger before and after the protection will be like in the photos below.

New coils	                   without protection		   with anti-corrosion protection

with anti-corrosion protection