Product specifications in italic shall be considered as key requirements.

SYSTEM DESCRIPTION

Factory assembled, air to water heat pump utilizing scroll compressors, low sound Greenspeed® variable-speed fans and optional hydronic pump module. The unit shall include all necessary wiring, piping, charge of R410A refrigerant, microprocessor controls and user display.

Note: Hydronic pump module shall be available with fixed-speed or Greenspeed® variable-speed driven pump(s).

QUALITY ASSURANCE

Unit shall be rated in accordance with EN14511-3 Standard, latest revision and unit performances shall be certified by independent Eurovent certification body. Unit without independent Eurovent certification shall be excluded.

Unit construction shall comply with European directives:

- Commission Regulation (EU) N° 813/2013 implementing Directive 2009/125/EC of the European Parliament and of the Council with regard to Eco-design requirements for space heaters and combination heaters

- Commission regulation (EU) N°327/2011 implementing Directive 2009/125/EC with regards to Eco-design requirements for industrial fans.

- Commission regulation (EU) N°640/2009 implementing Directive 2009/125/EC with regards to Eco-design requirements for electric motors.

- Commission regulation (EU) N°547/2012 implementing Directive 2009/125/EC with regards to Eco-

design requirements for water pumps (Unit equipped with hydronic module option).

- Pressurized equipment directive (PED) 2014/68/EC.

- Machinery directive 2006/42/EC, modified.

- Low voltage directive 2014/35/EC, modified.

- Electromagnetic compatibility directive 2014/30/EC, modified, and the applicable recommendations of European standards.

- Machine safety: electrical equipment in machines, general requirements, EN 60204-1.

Unit shall be manufactured in a facility registered to ISO 9001 Manufacturing Quality Standard and to ISO 14001 Environmental Management System. Unit shall be tested at the factory.

DESIGN PERFORMANCE DATA

Performance data certified by Eurovent independent body (mandatory).

- Cooling Capacity (kW): ………..*

- Heating Capacity (kW): ………..*

- SCOP according to EN14825: 3 2013 (kWh / kWh): ………..(average climate zone and water temperature  30οC/35oC)

- SEER according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  7οC/12oC)

- SEER according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  18οC/23oC)

- SEPR according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  7οC/12oC)

- Refrigerant type: R-410A

- Compressor tyrer: Scroll

- Number of Compressors: ….

- Hot water maximum leaving temperature:

- Evaporator Pressure Drop (kPa): ......

- Sound power level at full load (dB(A)): ……

- Sound pressure level 10m according to  ISO 4871 (dB (A)): ……

- Refrigerant amount : ...... .. kg (. ... Kg / kW)

- Dimensions, length x depth x height (mm): …… x …… x ……

- Unit operating weight: ….. kg

*Operating Conditions:

- Cold water inlet / outlet temperature (° C): ……..

- Hot water inlet / outlet temperature (° C): ……..

- Ambient temperature (° C) in cooling mode: ……..οC DB

- Ambient temperature (° C) in heating mode: ……..οC DB (RH 87%)

The above data shall be mentioned in the selection datasheet of the unit.

UNIT CONSTRUCTION

- Frame shall be of heavy-gage, painted galvanized steel painted in oven-baked polyester powder paint (light grey, RAL7035).

- Electrical Cabinet shall be galvanized steel casing painted in oven-baked polyester powder paint (light grey, RAL7035).

COMPRESSOR ASSEMBLY

- Fully hermetic scroll type compressors, each equipped with:

- Two-pole electric motor (Direct on line 400V, 2900rpm at 50Hz) cooled by suction gas and protected by internal temperature sensors.

- Initial oil charge of synthetic polyolester oil.

- Integral oil level sight glass.

- Electric crankcase heater to minimize oil dilution and refrigerant migration.

- Electronic over temperature motor protection.

- Optional soft starter to minimize compressor starting current with phase loss protection.

- Number of compressors:……

Low noise level and low vibration level shall be guaranteed by:

- Flexible anti-vibration mounts to isolate compressor assembly from unit chassis.

- Suction and discharge piping designed to prevent the transmission of vibrations to the unit chassis.

- Optional acoustic compressor enclosure, easily removable with 1/4 turn fasteners.

WATER HEAT EXCHANGER

- Brazed plate heat exchanger, direct expansion.

- Design shall incorporate of 2 independent direct-expansion refrigerant circuits connected in one water circuit..

- Plate exchangers shall be made of AISI 316L stainless steel, copper brazed type.

- Exchangers shall be thermally insulated with 19mm closed cell foam type insulation with a maximum K factor of 0.28.

- Shall be equipped with Victaulic-type fluid connections.

- Water heat exchanger shall be tested and stamped in accordance with European PED 97/23/EC Code.

- Water heat exchanger pressure drop shall not exceed 45 kPa under Eurovent conditions. Water heat exchanger with higher pressure drops shall be excluded.

- Water heat exchanger shall be provided with a factory-installed electronic flow switch.

AIR HEAT EXCHANGER

- Coil shall be air-cooled cupper tube aluminium fins heat exchanger (Cu/Al).

- Coil design shall adopt a V-shape for coil protection against hail damage. Vertical coils shall be excluded.

- Assembled coils shall be 100% leak tested and pressure tested at 45 bars.

FANS

- All fans on the unit shall controlled by variable frequency drive (with Greenspeed® intelligence) to provide higher part load efficiency and reduced acoustic levels.

- In Cooling mode, all fans shall be automatically controlled (Greenspeed® intelligence) to achieve higher part load efficiency, winter operation down to -20°C outside air temperature as standard, automatic fan speed adjustment in case of coil fouling, floating  condensing pressure, smooth fans start to increase unit lifetime and eliminate start/stop noise for sensitive acoustic applications.

- In Heating mode, all fans shall be automatically controlled (Greenspeed® intelligence) to achieve higher part load efficiency, fan speed adjustment in case of coil fouling or freezing, floating evaporator pressure, smooth fans start to increase unit lifetime and eliminate start/stop noise for sensitive acoustic applications.

- Each refrigerant circuit shall have a factory-installed, independent variable frequency drive. Variable speed drives shall be rated IP 55 enclosures and CE compliant.

- Air heat exchanger fans shall have a minimum overall efficiency higher than the minimum efficiency target to comply with commission regulation (EU) N°327/2011 implementing Directive 2009/125/EC with regards to Eco-design requirements for industrial fans.

- Air heat exchanger fans shall be direct-driven, 9-blade airfoil cross-section, reinforced polymer construction with inherent corrosion resistance, axial type, statically and dynamically balanced.

- Air shall be discharged vertically upward.

- Fans shall be protected by coated steel wire safety guards.

- Winter operation down to -20°C outside air temperature as standard in cooling mode.

REFRIGERANT

- HFC R410-A refrigerant

REFRIGERATION COMPONENTS

Each refrigerant circuit components shall include:

- Replaceable-core filter drier.

- Moisture indicating sight glass.

- Electronic expansion device.

- Liquid line service valves.

- Complete operating charge of refrigerant R-410A and compressor oil.

- Number of refrigerant circuits: 2

ELECTRIC FEATURES

- Unit shall operate on 400V, 3-phase, 50 Hz +/-10% power supply without neutral.

- Control voltage shall be supplied by a factory-installed transformer.

- Unit shall be supplied with factory-installed main circuit breaker, also  acting as electrical disconnect/isolator.

TOUCH PILOT CONTROL

The Touch Pilot Control includes advanced communication technology over Ethernet (IP), user-friendly and intuitive user interface with 5" color touch screen.

Advanced Control Features

- Web connectivity

- Fast BACnet IP connectivity (with “BACnet® IP Communication” option).

- Energy monitoring and trending capabilities (with “Electric energy meter” option).

- Alarm notification through emails.

- Trending capability (display by Web Browser only).

- Downloadable documentation (unit installation manual, control manual, spare-part list)

Touch Pilot, 5” User Interface

- Modern and intuitive 5 inch color screen.

- Finger or pencil touch capable.

- All local interaction accessible (Quick test, Start/Stop, Operating mode, …).

- Trending display.

- Synoptic screen with current operating status and physical values.

- 8 unicode languages supported including Chinese.

- Possibility to load a custom translation file.

- Access to the interface through Web Browser.

- Capacity to add up to two (2) user e-mail addresses for the automatic submission of fault reports.

Controls features

- Automatic circuit lead/lag.

- Refrigerant parameters control (suction superheat, condensing pressure control).

- Capacity control based on leaving (or entering) fluid temperature and compensated by rate of change of return-fluid temperature.

- Leaving or entering fluid temperature reset from outside air temperature, differential  water temperature or via a 0-10V signal.

- Provision of a dual set point for the leaving water temperature activated by a remote contact closure signal or by the built in time clock.

- Fluid temperature pull-down rate at start-up adjustable range from 0.11°C to 1.1°C per minute to prevent excessive demand spikes at start-up.

- Programmable seven-day time schedule. Up to 14 holiday period definitions.

- Night time sound reduction through demand limit and fan speed control to reduce the sound of the machine by a user-defined schedule.

- Equal run time rotation of compressors and pumps and number of starts.

- Demand limit control (configurable from 0% to 100 %) activated by remote contact closure.

- Remote system interlock.

- Alarm and Running outputs.

- Installation, Operation and Maintenance manual, and machine spares part list shall be available in   electronic format and easy accessible by connecting a laptop to the control panel.

- Unit water pump start/stop control.

- Water flow and external static pressure electronic calculation.

- Electronic setting of the water pump speed and the water flow (unit equipped with variable-speed pump hydronic module).

- Start/Stop command of external water pump (up to 2).

- Variable speed command of one external water loop pump by 0-10 V signal.

- Low ambient protection to energize Water heat exchanger and hydronic system trace heating (optional).

- Periodic pump start to ensure pump seals are properly maintained during off-season periods.

Control Diagnostics

Unit control display shall include the following information for fault diagnostics:

- Compressor lockout.

- Protection against loss of charge.

- Low fluid flow.

- Water heat exchanger freeze protection.

- Thermistor and transducer malfunction.

- Entering and leaving-fluid temperature.

- Water heat exchanger and air heat exchanger refrigerant pressure.

- Unit starts number and run hours.

- Compressor starts number and run hours.

- Fan starts number and run hours.

- Pump starts number and run hours.

- Quick test shall verify operation of every switch, fan, pump and compressor before chiller is started.

Diagnostics shall include the ability to view the list of the 10 alarms currently active with clear language descriptions of the alarm event.

- 2 alarm history buffers shall allow the user to store no less than 50 alarm events with clear language descriptions, time and date stamp event entry. One alarm history shall be dedicated to general alarms while the other shall only display major failures.

- The control system shall allow software upgrade without the need for new hardware modules.

Free defrost

Free defrost shall be provided in order to eliminate a relatively small amount of frost that has formed on the surface of the coil. Contrary to the standard defrost session; in the case of the free defrost session the heat (energy) shall be absorbed from the air. When running the free defrost, fans shall be activated and compressors shall be turned off. The free defrost is most efficient when the outside air temperature is above 1°C.

Safeties

Unit shall be equipped with thermistors / transducers and all other control devices to protect from the following:

- Reverse rotation or wrong electrical power connection.

- Low fluid temperature.

- Thermal overload.

- High Pressure control made by software and mechanical protection by pressure gauge opening.

- Low suction refrigerant pressure.

- Electrical overload.

- Loss of phase.

- Low voltage power supply failure.

- Low water flow rate.

OPERATING CHARACTERISTICS

Unit shall be capable of starting and running at outdoor ambient temperatures from -10°C to 48°C.

Unit shall be capable of starting up with 40°C entering fluid temperature to the Water heat exchanger.

ELECTRICAL CHARACTERISTICS

- Unit shall be supplied with main on/off disconnect switch without fuse.

- Single point power connection.

- Unit shall operate on 3-phase power supply at the voltage shown in the equipment schedule.

- Control points shall be accessed through terminal block.

- Unit shall be shipped with factory control and power wiring installed.

WATER CIRCUIT

Water circuit shall be rated for 10 bars maximum working pressure.

OPTIONS

The following options can be fitted to the unit, as required.

Hydronic module

- The hydronic module shall be integrated in the chiller chassis without increasing its dimensions and include the following elements: easily removable strainer, water pump with three-phase motor, accurate and reliable electronic water flow control (flow switch with paddle shall not be accepted), safety relief valve. Water flow and external static pressure electronic readings shall be available through operator user interface. Additional pressure/temperature taps (2) shall be factory installed to measure the pressure differential across the hydronic module.

- Water pump shall comply with Commission regulation (EU) N°547/2012 implementing Directive 2009/125/EC with regards to Eco-design requirements.

- Pump motors shall be totally enclosed single speed, 3-phase type with permanently lubricated bearings, Class F insulation. Pump motors shall be IE2/IE efficiency level rated.

- Each pump shall be 100% factory tested per Hydraulic Standards.

- The pump shall be protected against cavitation through electronic pressure control at pump inlet.

- Pump casing shall be of cast iron with cataphoresis coating.

- The impeller shall be of AISI 316L stainless steel laser technology welded.

- A choice of 6 hydronic modules shall be available:

- High-pressure single-pump hydronic module.

- High-pressure dual-pump hydronic module.

- Low-pressure single-pump hydronic module.

- Low-pressure dual-pump hydronic module.

- High-pressure variable-speed single-pump hydronic module.

- High-pressure variable-speed dual-pump hydronic module.

- Dual pump hydronic module shall have two independent electric motors and two independent impellers to ensure reliable operation.

- Cast iron body strainer with 1.2 mm mesh screen.

- The water piping shall be protected against corrosion and equipped with drain and vent plugs.

- The piping and the water pump shall be fully insulated to prevent condensation (pump insulation using polyurethane foam and painted steel casing).

- Frost protection down to -20°C shall be guaranteed by optional electric trace-heating  (24 volt) and the water pump shall be automatically started by the controller safety logic in case of a risk of frost formation.

- The customer connections shall be Victaulic connections.

Additional specifications for variable-speed pump hydronic module

- Hydronic module with variable-speed single pump shall be equipped with one VFD (variable frequency drive) to save energy.

- Hydronic module with variable-speed dual pump shall be equipped with two VFDs (variable frequency drive) for full redundancy and to save energy.

- VFD drive along with Greenspeed® intelligence shall be able to vary the pump motor speed in the 30-50 Hz frequency range.

- Nominal unit water flow shall be established through electronic setting of the pump speed to achieve energy savings. Use of a regulating valve to set nominal water flow shall not be accepted.

- Water flow control based on compressor usage, constant system pressure difference or constant system temperature difference shall be available on choice.

Expansion tank

Expansion tank shall be supplied with the hydraulic module to protect closed water systems from excessive pressure.

Water heat exchanger frost protection

Trace heating provides protection against Heat exchanger, water piping freezing between 0°C and –20°C outside air temperature.

Water heat exchanger and hydronic module frost protection

Trace heating provides protection against Heat exchanger, water piping and hydronic module freezing down to   -20°C outside air temperature.

Coil defrost resistance heaters

Electric heaters at the bottom of  air heat exchanger and the condensate pans to prevent from frost formation on the coils; compulsory in the heating mode, if the outdoor is below 0°C.

Welded water heat exchanger connection kit

Victaulic connection adapter for easy water piping connection.

Low noise level

Aesthetic and sound absorbing compressor enclosure to reduce noise level by 1 to 2 dB(A).

Very Low noise level

Aesthetic and sound absorbing compressor enclosure and fan speed limitation to reduce noise level by 5 to 6 dB(A) during cooling mode.

Partial heat reclaim

Unit equipped with one desuperheater on each refrigerant circuit for production of free high-temperature hot-water simultaneously with chilled or hot water production. Consist of one BPHE per refrigerant circuit to recover approximately 20% of the rejected heat for the production of hot water up to +65oC.

The unit shall operate in two modes:

- Efficiency priority mode

In this mode unit control optimizes unit efficiency. Heat reclaim is based on the saturated condensing temperature. The percentage of the reclaimed heating capacity compared with the total capacity rejected by the condenser increases in proportion to the saturated condensing temperature. This temperature is directly linked to the condenser entering air temperature.

- Reclaim priority mode

This configuration allows constant hot water leaving temperature regardless the unit operates at full or partial load. A setpoint is defined that is relative to the minimum condensing temperature to increase the heating capacity reclaimed at the desuperheaters.

Corrosion protection, traditional coils

Fins made of pre-treated aluminium (polyurethane and epoxy) for improved corrosion resistance, recommended for moderate marine and urban environments

Enclosure panels

Side enclosure panels at each end of the coil to improve aesthetics, to protect coil and piping against impacts.

Grilles and enclosure panels

Metal grilles on the 4 unit sides, plus side enclosure panels at each end of the coil to protect against intrusion to the unit interior, to improve aesthetics while protecting coil and piping protection against impacts.

Soft starter

Electronic starter on each compressor to reduce the start-up current.

Master/slave operation

- Two units connected by CCN shall cooperate to assure system water temperature.

- The master unit shall be the only interface to control the operation of both chillers.

- Up to 5 possible water loop configuration (parallel, common or dedicated pumps, series…).

- Three balance modes: Disabled, only on failure, according to run times.

- Common pump management (external pump and units provided with flow switch only) or dedicated pump management (internal pump can be used).

Energy management module

Communication board with additional inputs/outputs

Input contacts:

Set-point reset by indoor air temperature sensor (10 kohms) or by a 4 to 20 mA signal.

Time schedule override.

End of ice production (ice storage).

One additional demand limit volt-free input.

Demand limitation by 0-10 V signal.

Additional customer interlock

- -	Output contacts:

Instantaneous chiller capacity by 0-10 V signal.

Alert indicator.

Complete shut-down due to a chiller fault.

Boiler on/off command during winter season (heat mode by changeover or manual configuration).

Desuperheater customer water pump command ON/OFF.

4 Additional heating stages on/off command.

CCN to J-Bus gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a JBUS Local Area Network (JBUS, ModBUS). Field programming for customisation is possible.

CCN to Lon gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a LonWorks® Local Area Network (LON, i.e., LonWorks FT-10A ANSI/ EIA-709.1). Field programming shall be required.

BACnet/IP gateway (compatibility with Touch Pilot Control only)

Unit shall be supplied with factory-installed two-directional high-speed communication using BACnet protocol over Ethernet network (IP). This option shall allow unit integration with BACnet building automation system using Internet Protocol.  This new generation of BACnet IP communication shall allow high speed communications with building management systems, no limitation in reading/writing controller points and shall use standardized alarm codes as defined with BACnet protocol. Field programming may be required.

Electrical Plug

230V/0.8A AC power supply source provided with plug socket for connections of laptops.

Power Factor Correction 0.95

The automatic power factor correction will provide automatic regulation of unit power factor. The PFC consists of capacitors that are switched automatically by means of contactors.

High static fan for ducted application

The unit shall be equipped with high static fans up to 200Pa external static pressure available for ductwork

IP54 control boxes

The unit shall be equipped with IP54 control boxes

Water buffer tank module (for units with integrated hydronic module) .

Integrated water buffer tank underneath the unit

Capacity : 550 liters

Set point adjustment by 4-20mA signal.

Connections to allow a 4-20mA signal input.

Compressor discharge valves

The unit shall be equipped with shut-off valves per circuit on the compressor discharge piping.