Product specifications in italic shall be considered as key requirements.

SYSTEM DESCRIPTION

Factory assembled, air to water heat pump utilizing scroll compressors, fixed-speed fans and optional hydronic pump module. The unit shall include all necessary wiring, piping, charge of R410A refrigerant, microprocessor controls and user display.

Note: Hydronic pump module shall be available with fixed-speed or variable-speed driven pump(s) and include all the necessary components as described in hydronic module option.

QUALITY ASSURANCE

Unit shall be rated in accordance with EN14511-3 Standard, latest revision and unit performances shall be certified by independent Eurovent certification body. Unit without independent Eurovent certification shall be excluded.

Unit construction shall comply with European directives:

- Commission Regulation (EU) N° 813/2013 implementing Directive 2009/125/EC of the European Parliament and of the Council with regard to Eco-design requirements for space heaters and combination heaters

- Commission regulation (EU) N°327/2011 implementing Directive 2009/125/EC with regards to Eco-design requirements for industrial fans.

- Commission regulation (EU) N°640/2009 implementing Directive 2009/125/EC with regards to Eco-design requirements for electric motors.

- Pressurized equipment directive (PED) 2014/68/EC.

- Machinery directive 2006/42/EC, modified.

- Electromagnetic compatibility directive 2014/30/EC, modified, and the applicable recommendations of European standards.

- Machine safety: electrical equipment in machines, general requirements, EN 60204-1.

Unit shall be manufactured in a facility registered to ISO 9001 Manufacturing Quality Standard and to ISO 14001 Environmental Management System. Unit shall be tested at the factory.

DESIGN PERFORMANCE DATA

Performance data certified by Eurovent independent body (mandatory).

- Cooling Capacity (kW): ………..*

- Heating Capacity (kW): ………..*

- SCOP according to EN14825: 3 2013 (kWh / kWh): ………..(average climate zone and water temperature  30οC/35oC)

- SEER according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  7οC/12oC)

- SEER according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  18οC/23oC)

- SEPR according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  7οC/12oC)

- Refrigerant type: R-410A

- Compressor tyrer: Scroll

- Number of Compressors: ….

- Hot water maximum leaving temperature: 55 (° C)

- Evaporator Pressure Drop (kPa): ......

- Sound power level at full load (dB(A)): ……

- Sound pressure level 10m according to  ISO 4871 (dB (A)): ……

- Refrigerant amount : ...... .. kg (. ... Kg / kW)

- Dimensions, length x depth x height (mm): …… x …… x ……

- Unit operating weight: ….. kg

*Operating Conditions:

- Cold water inlet / outlet temperature (° C): ……..

- Hot water inlet / outlet temperature (° C): ……..

- Ambient temperature (° C) in cooling mode: ……..οC DB

- Ambient temperature (° C) in heating mode: ……..οC DB (RH 87%)

The above data shall be mentioned in the selection datasheet of the unit.

UNIT CONSTRUCTION

- Frame shall be of heavy-gage, painted galvanized steel painted in oven-baked polyester powder paint (light grey, RAL7035).

- Electrical Cabinet shall be galvanized steel casing painted in oven-baked polyester powder paint (light grey, RAL7035).

COMPRESSOR ASSEMBLY

- Fully hermetic scroll type compressors, each equipped with:

- Two-pole electric motor (Direct on line 400V, 2900rpm at 50Hz) cooled by suction gas and protected by internal temperature sensors.

- Initial oil charge of synthetic polyolester oil.

- Integral oil level sight glass.

- Electric crankcase heater to minimize oil dilution and refrigerant migration.

- Electronic over temperature motor protection.

- Optional soft starter to minimize compressor starting current with phase loss protection.

Low noise level and low vibration level shall be guaranteed by:

- Flexible anti-vibration mounts to isolate compressor assembly from unit chassis.

- Suction and discharge piping designed to prevent the transmission of vibrations to the unit chassis.

- Optional acoustic compressor jacket.

WATER HEAT EXCHANGER

- Brazed plate heat exchanger, direct expansion.

- For sizes over than 130kWatts,design shall incorporate a minimum of 2 independent direct-expansion refrigerant circuits connected in one water circuit.

- Plate exchangers shall be made of AISI 316 L stainless steel, copper brazed types.

- Heat exchangers shall be thermally insulated with 19mm closed cell foam type insulation.

- Shall be equipped with Victaulic-type fluid connections.

- Heat exchanger shall be tested and stamped in accordance with European PED 97/23/EC Code.

AIR HEAT EXCHANGER

- Vertical condenser coils

- Coil shall be air-cooled cupper tube aluminium fins heat exchanger (Cu/Al).

FANS

- Low-noise latest-generation Flying Bird IV fans, made of a composite material providing more quiet by not generating intrusive low-frequency noise

- Rigid fan installation for reduced start-up noise.

REFRIGERANT

- HFC R410-A refrigerant

REFRIGERANT CIRCUIT

- The unit shall include at least (…) compressors connected in parallel.

- Electronic expansion device (EXV) which allows operation at a lower condensing pressure (SCOP, SEER, SEPR optimisation).

- Dynamic superheat management for better utilisation of the water heat exchanger surface.

- Defrost cycle optimisation

ELECTRIC FEATURES

- Unit shall operate on 400V, 3-phase, 50 Hz +/-10% power supply without neutral.

- Control voltage shall be supplied by a factory-installed transformer.

- Unit shall be supplied with factory-installed main circuit breaker, also  acting as electrical disconnect/isolator.

TOUCH PILOT CONTROL

The Touch Pilot Control shall include advanced communication technology over Ethernet (IP), user-friendly and intuitive user interface with 4.3" colour touch screen shall provide the following features.

- Energy management

- Internal time schedule clock: Controls heat pump on/off times and operation at a second set-point

- Set-point offset based on the outside air temperature

- Master/slave control of two heat pumps operating in parallel with operating time equalisation and automatic change-over in case of a unit fault.

- Integrated advanced communication features

- Night mode: Capacity and fan speed limitation for reduced noise level

- For units with hydraulic module: Water pressure display and water flow rate calculation

- Easy and high-speed communication technology over Ethernet (IP) to a building management system

- Access to multiple unit parameters.

- For units without hydraulic module: 0-10V output shall be available for external variable speed pump controL

- 4.3’’ Touch Pilot user interface

- Intuitive and user-friendly 4.3 inch touch screen interface

- Concise and clear information shall be available in 6 languages (English, Spanish, French, German, Italian and a possibility to add a sixth one based on user’s preference)

- Complete menu, customised for different users (end user, service personnel or engineers).

- Capacity to add up to two (2) user e-mail addresses for the automatic submission of fault reports.

Remote management

Unit shall can be easily accessed with Touch Pilot control from the internet, using a PC with an Ethernet connection. This makes remote control quick and easy and offers significant advantages for service operations.

The unit shall be equipped with an RS485 serial port that offers multiple remote control, monitoring and diagnostic possibilities. The unit shall be also communicate with other building management systems via optional communication gateways.

A connection terminal allows remote control of the unit by wired cable as follows:

- Start/stop: Opening of this contact will shut down the unit

- Dual set-point: Closing of this contact activates a second set-point (example: unoccupied mode).

- Demand limit: Closing of this contact limits the maximum chiller capacity to a predefined value.

- Operation indication: This volt-free contact indicates that the chiller is operating (cooling load).

- Alarm indication: This volt-free contact indicates the presence of a major fault that has led to the shut-down of one or several refrigerant circuits.

Free defrost

Free defrost shall be provided in order to eliminate a relatively small amount of frost that has formed on the surface of the coil. Contrary to the standard defrost session; in the case of the free defrost session the heat (energy) shall be absorbed from the air. When running the free defrost, fans shall be activated and compressors shall be turned off. The free defrost is most efficient when the outside air temperature is above 1°C.

OPERATING CHARACTERISTICS

Unit shall be capable of starting and running at full or partial load as follows:

In heating mode at outdoor ambient temperatures from -15°C to 40°C as standard.

In cooling mode at outdoor ambient temperatures from -10°C to 48°C as standard.

ELECTRICAL CHARACTERISTICS

- Unit shall be supplied with main on/off disconnect switch without fuse.

- Single point power connection.

- Unit shall operate on 3-phase power supply at the voltage shown in the equipment schedule.

- Control points shall be accessed through terminal block.

- Unit shall be shipped with factory control and power wiring installed.

WATER CIRCUIT

Water circuit shall be rated for 10 bars maximum working pressure.

OPTIONS

The following options can be fitted to the unit, as required.

Brine options

Brine option for LWT from +5oC to 0°C

Allows production for LWT  from +5oC to 0°C

Brine option for LWT from 0oC to -15°C

Allows production for LWT  from 0oC to -12°C with propylene glycol (max. 45%) or from 0oC to -15°C with ethylene glycol (max. 45%).

Low sound level operation

Sound reduction from 1 to 6 dB(A) depending on the unit size and consists of 25mm thickness compressor jacket (all sizes) and 700 rpm fans (for sizes 060/070/078/140/160)

Compressor soft starter

Electronic starter on each compressor to reduce the start-up current.

Winter operation down to -20oC outdoor air temperature

Consist of one variable frequency drive (C2 class) to control the lead fan per circuit.

Anti-freeze protection down to -20oC outdoor air temperature (for unit with integrated hydronic module)

The frost protection of the heat pump water piping is guaranteed down to -20oC by automatically energized heaters and pump cycling. Heater for anti-freeze protection shall operate under 24V / 50W or 63W, supplied from the electrical panel of the unit.

Anti-freeze protection down to -20oC outdoor air temperature (for unit with integrated hydronic module and buffer tank))

The frost protection of the heat pump water piping is guaranteed down to -20oC by automatically energized heaters and pump cycling. Heater for anti-freeze protection shall operate under 24V / 50W or 63W, supplied from the electrical panel of the unit.

Partial heat reclaim

Unit equipped with one desuperheater on each refrigerant circuit for production of free high-temperature hot-water simultaneously with chilled or hot water production. Consist of one BPHE per refrigerant circuit to recover approximately 20% of the rejected heat for the production of hot water up to +65oC.

The unit shall operate in two modes:

- Efficiency priority mode

In this mode unit control optimises unit efficiency. Heat reclaim is based on the saturated condensing temperature. The percentage of the reclaimed heating capacity compared with the total capacity rejected by the condenser increases in proportion to the saturated condensing temperature. This temperature is directly linked to the condenser entering air temperature.

- Reclaim priority mode

This configuration allows constant hot water leaving temperature regardless the unit operates at full or partial load. A setpoint is defined that is relative to the minimum condensing temperature to increase the heating capacity reclaimed at the desuperheaters.

Master/slave operation

- Two units connected by CCN shall cooperate to assure system water temperature.

- System’s water temperature shall be controlled either by outlet or inlet temperature

- The master unit shall be the only interface to control the operation of both chillers.

- Three balance modes: Disabled, only on failure, according to run times.

Hydronic module

- The hydronic module shall be integrated in the heat pump chassis without increasing its dimensions and include the following elements: easily removable strainer, water pump, pressure relief valve, air purge, 2 drain valves, 2 pressure transducers to measure inlet/outlet pressure, 2 temperature probes to measure inlet/outlet water temperature.  The pump shall be protected against cavitation through electronic pressure control at pump inlet.

- A choice of 6 hydronic modules shall be available:

- High-pressure, fixed-speed, single-pump hydronic module.

- High-pressure, fixed-speed, dual-pump hydronic module.

- Low-pressure, fixed-speed, single-pump hydronic module.

- Low-pressure, fixed-speed, dual-pump hydronic module.

- High-pressure, variable-speed, single-pump hydronic module.

- High-pressure, variable-speed, dual-pump hydronic module.

Additional specifications for variable-speed pump hydronic module

The hydronic module shall include pressure transducers that permit intelligent measurement of the water flow rate and real-time display on the user interface. All adjustments shall be made directly on the interface, speeding up start-up and maintenance.

Operating logic

Full-load set point

The flow rate control at full load uses the user interface, reducing the pump speed.

Operating mode at part load

Two part-load operating modes shall be included:

- Constant outlet pressure control

The control shall continuously act on the pump speed to ensure a constant outlet pressure.

- Constant delta T control.

The Variable Water Flow algorithm shall maintain a constant delta T no matter what the unit load, reducing the flow rate to the minimum.

Expansion tank

Expansion tank shall be supplied with the hydraulic module to protect closed water systems from excessive pressure.

Corrosion protection, traditional coils

Fins made of pre-treated aluminium (polyurethane and epoxy) for improved corrosion resistance, recommended for moderate marine and urban environments

CCN to J-Bus gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a JBUS Local Area Network (JBUS, ModBUS). Field programming for customisation is possible.

CCN to Lon gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a LonWorks® Local Area Network (LON, i.e., LonWorks FT-10A ANSI/ EIA-709.1). Field programming shall be required.

BACnet

Unit shall be supplied with factory-installed two-directional high-speed communication using BACnet protocol.

External boiler management

Control board factory-installed on the unit to control a boiler.

Electric heaters management

Control board factory-installed on the unit with additional inputs/outputs in order to manage up to 4 externals heating stage (electrical heaters…)

Reinforced ECM filtration for fan VFD

Fan variable frequency drive compliance to IEC 61800-3 C1 class

Reinforced ECM filtration for pump VFD

Pump variable frequency drive compliance to IEC 61800-3 C1 class.

Water buffer tank module (for units with integrated hydronic module) .

Integrated water buffer tank underneath the unit

Capacity : 250 liters

Set point adjustment by 4-20mA signal.

Connections to allow a 4-20mA signal input.