General description

Water-cooled (30RW) or condenserless (30RWA) liquid chiller for indoor installation, equipped with scroll compressors, auto-adaptive microprocessor control and operating with HFC-407C refrigerant that has no effect on the ozone layer.

Quality assurance

Unit construction shall comply with European directives:

- Machinery directive 98/37/CE, modified.

- Low voltage directive 73/23/EEC, modified,

- Electromagnetic compatibility directive 89/336/EEC, modified and with the applicable recommendations of European standards:

- Machine safety, electrical equipment in machines, general regulations: EN 60204-1.

- Radiated electromagnetic emissions: EN 50081-1,

- Conducted electromagnetic emissions: EN 50081-2,

- Electromagnetic immunity EN 50082-2.

Unit shall be designed, manufactured and tested in a facility with a quality management system certified ISO 9001 and environmental management system ISO 14001.

Unit shall be run tested at the factory.

Design performance data

- Cooling capacity (kW): ……

- Unit power input (kW): ……

- Full load energy efficiency, EER (kW/kW): ……

- Part load energy efficiency, ESEER (kW/kW): ……

- Evaporator entering/leaving water temperature (°C): … /

- Fluid type: …….

- Fluid flow rate (l/s): ……

- Evaporator pressure drops (kPa): ……

- Condenser entering/leaving water temperature (°C): ……

- Fluid type: …….

- Fluid flow rate (l/s): ……

- Condenser pressure drops (kPa): ……

- Sound power level at full load (dB(A)): ……

- Dimensions, length x depth x height (mm): … x … x

- Number of compressors

Frame

Chassis and cabinet made of galvanised sheet steel. Painted in oven-baked polyester powder paint in light grey colour (RAL 7035). Removable side and rear panels. Front access via hinged doors.

Compressor

- Unit shall have Hermetic scroll compressor driven by direct drive of 2-pole electric motor.

- Motor is cooled by a  suction gas , passing over the motor windings.

- Motor has overload protection through an internal thermostat.

- The compressors are installed and fixed with anti-vibration mounts to minimize vibration transfer within the unit .

- Compressors have polyolester synthetic oil charge, and oil level sight glass.

Evaporator

Stainless steel plate heat exchanger with welded copper connections. From size 30RW 160 upwards the evaporator has two interlaced independent refrigerant circuits. Closedcell thermal foam insulation.

Condenser (30RW only)

Stainless steel plate heat exchanger with welded copper connections. From size 30RW 160 upwards the condenser has two interlaced independent refrigerant circuits.

Refrigerant circuit

Each circuit includes:

- One or two compressors

- Liquid linevalve,

- Moisture sight glass,

- Filter drier,

- Thermostatic expansion device,

- High and low pressure transducers,

- Manuallyreset high pressure switch,

- High and low-pressure safety valve (except sizes 30RW 020-045) and

- HFC-407C refrigerant charge.

The main components of the refrigerant circuit are welded.

On 30RWA units the refrigerant circuit also includes a check valve on the discharge piping, a solenoid valve on the liquid piping, refrigerant piping and a nitrogen holding charge.

Control and power circuit control box

- The control box is accessible via a hinged door. It includes a main disconnect switch, fuses and circuit breakers, compressor and evaporator water pump contactors, thermal relays, low-voltage control circuit transformer (24 V control circuit) and the Pro-Dialog control system. The whole unit is supplied via a single power connection point (three-phase supply without neutral).

- Extraction fans protecting the electrical components against overheating.

Evaporator hydronic module

The hydronic module shall be integrated in the unit and include the following elements:

- Removable screen filter.

- Expansion tank.

- Single monocell centrifugal water pump.

- Three-phase motor with internal thermal protection.

- Water flow switch.

- Safety valve

- Flow control valve.

- Pressure gauge and purge valves.

- Internal piping made of galvanised steel.

- Thermal piping and water pump insulation to prevent condensation.

- Victaulic water connections at the top (30RW 110-150) or on the right-hand side (30RW 160-300) with welded connection sleeve.

Note: Units without hydronic module (standard): water flow switch installed as standard and water piping protected against condensation.

Condenser hydronic module

The hydronic module shall be integrated in the unit and include the following elements:

- Removable screen filter.

- Expansion tank

- Single monocell centrifugal water pump

- Three-phase motor with integrated frequency converter.

- Safety valve

- Pressure gauge and purge valves.

- Internal piping made of galvanised steel with thermal insulation.

- Victaulic water connections at the top (30RW 110-150) or on the right-hand side (30RW 160-300) with welded connection sleeve.

Control system

Pro-Dialog Plus ensures the following functions:

- Entering or leaving chilled or hot water (heat pump option) temperature control by PID loop with compressor run time and start-up equalising. The system permanently adjusts the system inertia and ensures complete protection against excessive compressor cycling.

- Head pressure control by auto-adaptive algorithm:

- Control of the frequency converter, integrated into the condenser water pump

- Activating a maximum of 8 fan stages with operating time equalising or fan speed control .

- Fan rotation speed control (with Carrier air-cooled condenser)

- Evaporator and condenser water pump control (optional dual pump with automatic change-over in case of a fault from size 30RW 110 upwards).

- Control at the second setpoint (example: unoccupied room).

- Leaving water temperature reset, based on the air temperature

(with Carrier glycol cooler or air-cooled condenser) or the difference between entering/leaving water temperature.

Operator interface

Includes status or fault LEDs, two numerical displays, a refrigerant system synoptic diagram and a command keyboard.

- Immediate display of parameters: entering/leaving chilled water temperature, compressor suction/discharge pressures and temperatures, setpoint, run times and number of compressor start-ups.

- Diagnosis and complete parameter set by selection of one of the following ten menus: information, temperatures, pressures, setpoints, input values, test, configuration, alarms, alarm history and run times.

Remote chiller management

Volt-free contact inputs permit:

- Start/stop control

- Selection of cooling or heat reclaim mode (override mode at high condensing temperature)

- Integration of a customer safety device

- Operation at the second setpoint* (example: room unoccupied)

- Maximum demand limit* (three limit levels from size 30RW 160 upwards)

Outputs are available for:

- Start-up of a boiler

- Signalling of a general fault condition for each circuit.

Note: For units without hydronic module (standard) a 0-10 V output is available to control a three-way valve or a variablespeed condenser water pump.

The optional CCN Clock Board permits:

- Control in master/slave configuration of two chillers operating in parallel

- Programming of operating time schedules (up to 8 periods per week)

- Programming of operating time schedules for the second setpoint (up to 8 periods per week)

- Definition of an operating time period with a reduced number of fans (for example during the night)

- Definition of an operating time period with demand limitation

- Integration of the chiller into a building monitoring system (BMS): serial port RS 485.

Safeties

The system checks the evolution of the parameters (temperatures, pressures etc.), and responds to maintain the compressor within the operating range. If despite this one parameter exceeds its limit, an alert message is generated or the unit is shut down. The following faults cause the refrigerant circuit or the unit to be shut down:

- Low suction pressure

- High discharge pressure

- Low suction temperature

- Compressor, water pump overload

- Reverse compressor rotation

- Temperature sensor and pressure transducer fault

- Board and loss of communication fault

- Customer safety device tripping

- Water heat exchanger anti-freeze protection

- More than 50 alert or fault codes to facilitate fault detection.