General description

Water-cooled (30WG) liquid chiller for indoor installation, equipped with scroll compressors, Pro-Dialog+ control and operating with R-410a refrigerant that has no effect on the ozone layer.

Quality assurance

The design and manufacturing site of the units shall be certified in accordance with the quality management system ISO 9001.

The development test site of the units shall be certified to the quality management system ISO 17025.

The design and manufacturing site of the units shall be certified in accordance with the environmental management system ISO 14001.

The manufacturing site is certified ISO 50001 (Energy management system).

The published performances for the units shall be Eurovent-certified and all units are factory-tested before shipment.

The units shall meet the following product quality standards: 2014/35/UE, 2014/30/UE, 2014/68/UE, 2011/65/UE "RoHS 2", 2012/19/EU "WEEE", 2009/125/EC "Ecodesign", EN14511.

Design performance data

- Cooling capacity (kW): ……

- SEER 12/7°C Comfort low temp:		kWh/kWh

- SEER 23/18°C Comfort medium temp:		kWh/kWh

- SEPR 12/7°C Process high temp:		kWh/kWh

- SCOP (Low 30°C/35°C):		kWh/kWh

- SCOP (Medium 47°C/55°C)*:		kWh/kWh

- Evaporator entering/leaving water temperature (°C): … /

- Fluid type: …….

- Fluid flow rate (l/s): ……

- Evaporator pressure drops (kPa): ……

- Condenser entering/leaving water temperature (°C): ……

- Fluid type: …….

- Fluid flow rate (l/s): ……

- Condenser pressure drops (kPa): ……

- Sound power level at full load (dB(A)): ……

- Dimensions, length x depth x height (mm): … x … x

- Number of compressors

The unit shall be capable of starting with up from 7.5 °C up to 27 °C entering water temperature to the evaporator.

The unit shall be capable of starting with up from 15 °C up to 55 °C entering water temperature to the condenser. For a condenser with an entering temperature below 15 °C the use of a three way valve recommended.

The unit shall operate with condenser leaving water temperature from 20 °C.up to 60 °C.

The unit shall operate with evaporator leaving water temperature from 5 °C up to 20 °C.

(Carrier option 6) The unit shall permit chilled brine solution production down to -12 °C when ethylene glycol is used..

The pressure control signal will ensure safe unit operation and maximised performance at low sourceside

water temperatures.

Frame

Chassis and cabinet made of galvanised sheet steel. Painted in oven-baked polyester powder paint in light grey colour (RAL 7035). Removable side and rear panels.

The unit shall have water connections at the top/back.

Compressor

- Unit shall have Hermetic scroll compressor driven by direct drive of 2-pole electric motor.

- Motor is cooled by a  suction gas , passing over the motor windings.

- Motor will have overload protection through an internal thermostat.

- The compressors will have been installed and fixed with anti-vibration mounts to minimize vibration transfer within the unit .

- Compressors will have polyolester synthetic oil charge, and oil level sight glass.

Dangerous compressor cycles are reduced to six per hour.

(Carrier option 25) Consists of an electronic soft-starter per compressor. This permits optimizing the start-up current, and reducing nuisance cut-outs due to current surges in the electrical system at start-up.

(Carrier option 257) Compressor and oil separator sub-assembly and refrigerant gas suction line shall be acoustically insulated

Evaporator

The unit will have stainless steel direct-expansion plate heat exchanger with Victaulic connections. The  max. water-side operating pressure is 1000 kpa.

Condenser

The unit will have stainless steel plate heat exchanger with Victaulic connections. From size 30WG 50 upwards the condenser has two interlaced independent refrigerant circuits. The  max. water-side operating pressure is 1000 kpa.

(Carrier option 86) There is an additional thermal insulation in the condenser , optimized for heating applications.

Refrigerant circuit

Each circuit will include:

- One or two compressors

- Liquid linevalve,

- Moisture sight glass.

- Filter drier.

- Thermostatic expansion device,

- High and low pressure transducers.

- Manuallyreset high pressure switch,

- R-410a refrigerant charge.

The refrigerant circuit components of the unit shall be compatible with a condenser leaving water temperature of 65 °C.

Control and power circuit control box

- The unit shall operate with 400 V-3 ph-50 Hz (400 V ± 10%) without neutral and it shall only have one connection point

- The main control panel shall be protected by a glass panel and shall only be opened with a special tool.

- The unit control circuit voltage shall be 24 V maximum, supplied by a factory-installed transformer. The compressor shall offer quick keyed electrical connection

- The control menus shall permit direct access do all unit data including the history of possible faults.

(Carrier option 70F) The handle of the electrical disconnect switch is on the outside of the unit

Evaporator hydronic module

The original pumps that are factory-installed in these units have motors with efficiency class IE2.

The hydronic module is located in the upper unit section.

There are two hydronic module available:

(Carrier option Option 116T): Evaporator hydronic module equipped with low pressure fixedspeed pump, drain valve, air vent and pressure sensors.

(Carrier option Option 116V): Evaporator hydronic module equipped with high-pressure variable-speed pump, drain valve, air vent and pressure sensors.:

(Carrier option Option 293) :The hydronic module includes screen filter, expansion tank and safety valve integrated in the evaporator hydronic module.

Note: Units without hydronic module (standard): water flow switch installed as standard .

Condenser hydronic module

The original pumps that are factory-installed in these units have motors with efficiency class IE2.

The hydronic module is located in the upper unit section.

(Carrier option Option 270T): Condenser hydronic module equipped with low pressure fixedspeed pump, drain valve, air vent and pressure sensors.

(Carrier option Option 270V): Condenser hydronic module equipped with high-pressure variable-speed pump, drain valve, air vent and pressure sensors.

(Carrier option Option 293A) :The hydronic module includes screen filter, expansion tank and safety valve integrated in the condenser hydronic module.

Controls

The Touch Pilot Control shall include advanced communication technology over Ethernet (IP), user-friendly and intuitive user interface with 4.3" colour touch screen shall provide the following features.

- Energy management

- Internal time schedule clock: Controls heat pump on/off times and operation at a second set-point

- Set-point offset based on the outside air temperature

- Master/slave control of two heat pumps operating in parallel with operating time equalisation and automatic change-over in case of a unit fault.

- Integrated advanced communication features

- Night mode: Capacity and fan speed limitation for reduced noise level

- For units with hydraulic module: Water pressure display and water flow rate calculation

- Easy and high-speed communication technology over Ethernet (IP) to a building management system

- Access to multiple unit parameters.

- For units without hydraulic module: 0-10V output shall be available for external variable speed pump controL

- 4.3’’ Touch Pilot user interface

- Intuitive and user-friendly 4.3 inch touch screen interface

- Concise and clear information shall be available in 6 languages (English, Spanish, French, German, Italian and a possibility to add a sixth one based on user’s preference)

- Complete menu, customised for different users (end user, service personnel or engineers).

Remote management

Unit shall can be easily accessed with Touch Pilot control from the internet, using a PC with an Ethernet connection. This makes remote control quick and easy and offers significant advantages for service operations.

The unit shall be equipped with an RS485 serial port that offers multiple remote control, monitoring and diagnostic possibilities. The unit shall be also communicate with other building management systems via optional communication gateways.

A connection terminal allows remote control of the unit by wired cable as follows:

- Start/stop: Opening of this contact will shut down the unit

- Dual set-point: Closing of this contact activates a second set-point (example: unoccupied mode).

- Demand limit: Closing of this contact limits the maximum chiller capacity to a predefined value.

- Operation indication: This volt-free contact indicates that the chiller is operating (cooling load).

- Alarm indication: This volt-free contact indicates the presence of a major fault that has led to the shut-down of one or several refrigerant circuits.

- (Carrier option 148B) A two-directional communication board shall allows plug and play interfacing of the machine with any BMS using the J-Bus protocol.

- (Carrier option 148C) A two-directional communication board shall allows plug and play interfacing of the machine with any BMS using the BacNet protocol

- (Carrier option 148D) A two-directional communication board shall allows plug and play interfacing of the machine with any BMS using the LonTalk protocol

Safeties

A patented auto-adaptive algorithm controls compressor operation and permanently adapts to the

system charac-teristics (water loop inertia). Dangerous compressor cycling is prevented.

Control permanently analyses the compressor suction and discharge pressures and temperatures. If an

abnormal situation is detected, the control reacts, e.g. by reducing the capacity. As a result the compressors always operate in their ideal temperature range and many unit shut-downs due to a fault can be prevented.

(Carrier option 58) Unit equipped with an additional field-installed leaving water temperature sensor, allowing master/slave operation of two units connected in parallel.

Master/slave operation

- Two units connected by CCN shall cooperate to assure system water temperature.

- The master unit shall be the only interface to control the operation of both chillers.

- Up to 5 possible water loop configuration (parallel, common or dedicated pumps, series…).

- Three balance modes: Disabled, only on failure, according to run times.

- Common pump management (external pump and units provided with flow switch only) or dedicated pump management (internal pump can be used).