General description

(30XW-PZE / 30XWHPZE) Factory assembled single piece water-cooled chiller, shall include all factory wiring, piping, controls, refrigerant charge (HFO-1234ze), refrigeration circuits, screw compressors, electronic expansion valves and equipment required prior to field start-up.

(30XWHZE / 30XWHPZE) Factory assembled single piece water-sourced heat pump, shall include all factory wiring, piping, controls, refrigerant charge (HFO-1234ze), refrigeration circuits, screw compressors, electronic expansion valves and equipment required prior to field start-up.

Quality assurance

Unit shall be rated in accordance with EN14511-3 Standard, latest revision and unit performances shall be certified by independent Eurovent certification body. Unit without independent Eurovent certification shall be excluded.

Unit construction shall comply with European directives:

- From 1st January 2018, commission regulation (EU) N°2016/2281 implementing Directive 2009/125/EC of the European Parliament and of the Council with regards to Ecodesign requirements for ENER Lot 21 comfort cooling chillers

- Commission Regulation (EU) N° 813/2013 implementing Directive 2009/125/EC of the European

- Parliament and of the Council with regard to Eco-design requirements for space heaters and combination heaters

- Pressurized equipment directive (PED) 2014/68/EU

- Machinery directive 2006/42/EC, modified

- Low voltage directive 2014/35/EC, modified

- Electromagnetic compatibility directive 2014/30/EC (modified) and the applicable recommendations of European standards

- Machine safety: electrical equipment in machines, general requirements, EN 60204-1

- Electromagnetic compatibility emission EN61000-6-4

- Electromagnetic compatibility immunity EN61000-6-2

- Unit shall be designed, manufactured and tested in a facility with a quality management system certified ISO 9001 and environmental management system ISO 14001.

- Unit shall be run tested at the factory.

Design performance data

Performance data certified by Eurovent independent body (mandatory).

-	Cooling Capacity (kW): ………..*

-	Heating Capacity (kW): ………..*

-	SCOP according to EN14825: 3 2013 (kWh / kWh): ………..(average climate zone and water  temperature  30οC/35oC)

- SCOP according to EN14825: 3 2013 (kWh / kWh): ………..(average climate zone and water  temperature  47οC/55oC)

-	SEER according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  7οC/12oC)

-	SEER according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  18οC/23oC)

-	SEPR according to EU 2016 / 2281 (kWh / kWh): ……….. (water temperature  7οC/12oC)

-	Refrigerant type: R-1234ze (GWP < 1)

-	Compressor type: Semi-hermetic screw compressors

-	Number of Compressors: ….

- Number of refrigerant circuits: …

-	Hot water maximum leaving temperature:

-	Evaporator Pressure Drop (kPa): ......

- Evaporator Fluid flow rate (l/s): ……

- Condenser Pressure Drop (kPa): ......

- Condenser Fluid flow rate (l/s): ……

-	Sound power level at full load (dB(A)): ……

-	Refrigerant amount : ...... .. kg (. ... Kg / kW)

-	Dimensions, length x depth x height (mm): …… x …… x ……

-	Unit operating weight: ….. kg

*Operating Conditions:

Cooling

-	Evaporator cold water inlet / outlet temperature (° C): ……..

-	Condenser hot water inlet / outlet temperature (° C): ……..

Heating

-	Evaporator cold water inlet / outlet temperature (° C): ……..

-	Condenser hot water inlet / outlet temperature (° C): ……..

The above data shall be mentioned in the selection datasheet of the unit.

Performance shall be declared in accordance with EN14511-3:2013 and certified by Eurovent up to 1500 kW.

The unit shall be capable of starting with 13 °C entering water temperature to the condenser with condenser head pressure control option. The unit shall be capable of starting with 35 °C entering water temperature to the evaporator.

The machine shall operate with condenser leaving water temperature up to 55 °C.

- (Carrier option 150) The unit shall operate with condenser leaving water temperature up to 70 °C.

- (Carrier option 8) The unit shall permit chilled brine solution production down to -3 °C when ethylene glycol is used, or down to 0°C when propylene glycol is used.

Frame

- Machine frame shall include heat exchangers and compressors in a self-supporting structure

- Electrical panel doors shall be accessible by 1/4-turn screws

Compressor

- Unit shall have semi-hermetic twin-screw compressors with internal relief valve and check valve to avoid reverse rotation on shut down

- Each compressor shall be equipped with a discharge shut-off valve

- The discharge shall also be equipped with a muffler to reduce discharge gas pulsations

- Compressor bearings shall be designed for minimum 73000 hours at maximum operating conditions

- Capacity control shall be provided by a slide valve

- Compressor capacity control shall be step-less from 100% to 15% load

- Compressor shall start in unloaded condition

- Motor shall be cooled by suction gas and protected through a dedicated electronic board against the following: thermal overload by internal winding temperature sensors, electrical overload and short circuit by dedicated fuses (one per phase), reverse rotation, loss of phase, under-voltage and power supply failure

- Lubrication oil system shall include pre-filter and external filter capable of filtration to 5 microns

- The oil filter line shall be equipped with service shut off valves for easy filter replacement

- The oil separator, shall be integrated in the condenser design and shall not require oil pump

- The oil separator shall include an oil level safety switch.

Evaporator

- Unit shall be equipped with a single flooded evaporator

- Evaporator shall be manufactured by the chiller manufacturer

- Evaporator shall be tested and stamped in accordance with the European directive for pressurized equipment 97/23/EC

- The maximum refrigerant-side operating pressure will be 2100 kPa, and the maximum waterside pressure will be 1000 kPa (2100kPa as an option)

- The evaporator shall be mechanically cleanable, shell and-tube type with removable heads

- Tubes shall be internally and externally grooved, seamless-copper, and shall be rolled into tube sheets

- Shell shall be insulated with 19 mm closed-cell foam with a maximum K factor of 0.28. Evaporator thermal insulation shall be factory fitted

- The evaporator shall have a drain and vent in each head

- Chiller shall have only one water inlet & outlet connection with Victaulic couplings to avoid vibrations transmission and to accommodate minor pipework misalignment (Victaulic adapter kit shall be available on demand)

- The evaporator shall incorporate an indirect refrigerant level control system (based on the continuous measurement of the approach value) to ensure optimum heat transfer performance under all load conditions

- Design shall incorporate either 1 or 2 independent refrigerant circuits

- Evaporator shall be fitted with electronic auto setting water flow switch. Paddle switches or differential pressure switches shall not be acceptable.

Condenser

Unit shall be equipped with a single condenser

- Condenser shall be manufactured by the chiller manufacturer

- Condenser shall be tested and stamped in accordance with the European directive for pressurized equipment 97/23/EC

- Single pass or 2-passes design shall be possible

- The maximum refrigerant-side operating pressure will be 2100 kPa, and the maximum waterside pressure will be 1000 kPa (2100kPa as an option)

- The condenser shall be mechanically cleanable shell and-tube type with removable heads

- Tubes shall be internally and externally grooved, seamless-copper, and shall be rolled into tube sheets

- The condenser shall have a drain and vent in each head

- Chiller shall have only one water inlet & outlet connection with Victaulic couplings to avoid vibrations transmission and to accommodate minor pipework misalignment (Victaulic adapter kit shall be available on demand)

- Design shall incorporate either 1 or 2 independent refrigerant circuits plus the oil separator.

Refrigerant circuit

- Refrigerant circuit components shall include: compressor, oil separator, high and low side pressure relief devices, economizer, filter driers, moisture indicating sight glasses, long stroke electronic expansion device, and complete operating charge of both refrigerant R-1234ze and compressor oil

- (Carrier option 92) A compressor suction and discharge line shut off valve, an evaporator inlet valve and economizer line valve, shall be mounted to isolate all main components (filter drier, oil filter, expansion device and compressor) and allow refrigerant to be safely stored during service operation

- (Carrier option 257) Evaporator and refrigerant gas suction line shall be acoustically insulated.

Power control box

- Unit shall be supplied with specific electrical box with increased tightness, integrated blower and fresh air duct connection to maintain positive air pressure to avoid any risk of ignition.

- Unit shall operate at 400 Volts (+/- 10%), 3-phases, 50 Hertz power supply without neutral

- Unit shall be designed for simplified connection on TN(s) networks

- Control circuit voltage shall be 24 V maximum, supplied by a factory-installed transformer

- Unit shall be supplied with factory-installed main circuit breaker/isolator

- Unit shall have single point power connection (Carrier option 81 for sizes 1002/1762)

- Unit shall have a factory installed star/delta starter as standard to limit electrical inrush current

- Power control box is powered painted with hinged and gasket sealed doors and is protected to IP23.

Controls

- Unit control shall include as a minimum: microprocessor with non-volatile memory, picture guided unit/operator interface, the LOCAL/OFF/REMOTE/CCN selector and a 5 inches colored touch-screen display with multiple language capability

- Pressure sensors shall be installed to measure suction, discharge, and oil pressure

- Temperature probes shall be installed to read cooler/condenser entering and leaving temperatures.

- (Carrier option 158A) Unit control shall include as a minimum: microprocessor with non-volatile memory, picture guided unit/operator interface, the LOCAL/OFF/REMOTE/CCN selector and a 7 inches colored touch-screen display with multiple language capability

- Unit control shall have an IP port to permit user connection via web browser, allowing same level of access to control menus as unit mounted interface (excluding start/stop and alarm reset capabilities)

- Control shall store technical documentation, drawings and spare parts list specific to each particular unit

- (Carrier option 148B) A two-directional communication board shall allow plug and play interfacing of the machine with any BMS using the J-Bus protocol

- (Carrier option 148D) A two-directional communication board shall allow plug and play interfacing of the machine with any BMS using the LonTalk protocol

- (Carrier option 149) Machine shall be supplied with factory-installed two-directional high-speed communication using BACnet protocol over Ethernet network (IP-connection). The BACnet over-IP communication shall have no limitation in reading/writing controller points and shall use standardized alarm codes as defined with BACnet protocol. Filed programming shall be required.

- (Carrier option 298) Machine shall be accessible via wireless connection for remote monitoring with the scope of preventive maintenance.

Unit shall be capable of performing the following functions:

- Electronic expansion valve control optimizing evaporator refrigerant charge while ensuring minimum refrigerant superheat and optimum sub-cooling at condenser outlet

- Capacity control based on leaving chilled fluid temperature

- Limitation of the chilled fluid-temperature pull-down rate at start-up to an adjustable range of 0.1°C to 1.1°C per minute to prevent excessive demand spikes at start-up

- Automatic change-over and cycling of compressors to equalize running hours and number of starts

- Reset enable of leaving chilled-water temperature based on the outdoor air temperature or via a 4-20 mA signal (as option)

- Dual set point management for the leaving chilled water temperature activated by a remote contact closure signal or by the built in time clock

- 2-level demand limit control (between 0 and 100%) activated by remote contact closure or by the built in time clock

- Time scheduling management to enable unit start-up control, demand limit and set-point changes

- Trending of main variables

- Capacity to add up to two (2) user e-mail addresses for the automatic submission of fault reports.

- (Carrier option 58) lead/lag type control of two chillers running in series or parallel

- (Carrier option 84) Water pump control, safety pumps (if installed) on both condenser and cooler side

- (Carrier option 156) The following inputs contacts shall be available on the unit control board:

- Set-point reset by indoor air temperature sensor

- Cooling set-point reset by 4-20 mA

- Time schedule override

- Ice storage input

- Demand limit

- Unit shut down

The following outputs contacts shall be available on the unit control board:

- Instantaneous chiller capacity by 0-10 V signal

- Complete shut-down due to a chiller fault

- Compressor operation indication.

Diagnosis

- Control interface shall be capable of displaying set-points, system status including temperatures, pressures, current for each compressor, run time and percent loading

- Control interface shall perform trending of up to 10 preselected variables

- Control system shall allow a quick test of all machine elements to verify the correct operation of every switch, circuit breaker, contactor etc. before the chiller is started

- In case of alarm, control system shall send an email to specific mail box set by user during machine commissioning

- Control shall have black box function which permit to store data set of 20 variables with interval of 5 seconds during 14 minutes before the alarm and 1 minute following the alarm event. The black box recording capability shall permit recording for 20 events and once the threshold is reached new data shall over-write the oldest ones.

Safeties

- Control system shall provide the unit with protection against the following:

- Reverse rotation

- Low chilled water temperature

- Low oil pressure (per compressor)

- Current imbalance

- Compressor thermal overload

- High pressure (with automatic compressor unloading in case of excessive condensing temperature)

- Electrical overload and short circuit

- Loss of phase, under-voltage and power supply failure

Control shall provide separate general alert (minor incident) and alarm (circuit down) remote indication.