General description

(30XW-VZE) Factory assembled single piece water-cooled chiller, shall include all factory wiring, piping, controls, refrigerant charge (R-1234ze), refrigeration circuits, inverter-driven screw compressors, electronic expansion valves and equipment required prior to field start-up.

(30XWHVZE) Factory assembled single piece water-sourced heat pump, shall include all factory wiring, piping, controls, refrigerant charge (R-1234ze), refrigeration circuits, inverter driven screw compressors, electronic expansion valves and equipment required prior to field start-up.

HFO-1234ze is an energy-efficient alternative to traditional refrigerants.  HFO-1234ze is a medium pressure, low GWP refrigerant with the below advantages:

- Lower discharge pressure results in less mechanical stress, thus extending the life of the compressor.

- Higher energy efficiency.

- Reduces direct and indirect CO2 emissions.

- Safer in use.

Quality assurance

Unit construction shall comply with European directives:

- Commission Regulation (EU) N° 813/2013 implementing Directive 2009/125/EC of the European Parliament and of the Council with regard to Eco-design requirements for space heaters and combination heaters

- Pressurized equipment directive (PED) 97/23/EC

- Machinery directive 2006/42/EC, modified

- Low voltage directive 2006/95/EC, modified

- Electromagnetic compatibility directive 2004/108/EC modified, and the applicable recommendations of European standards

- Machine safety: electrical equipment in machines, general requirements, EN 60204-1

- Electromagnetic compatibility immunity EN61000-6-2

- Electromagnetic compatibility emission EN 61800-3,Category C3

- (Carrier option 282) Electromagnetic compatibility emission EN61800-3,C2 Category.

Unit shall be designed, manufactured and tested in a facility with a quality management system certified ISO 9001 and environmental management system ISO 14001. Unit shall be run tested at the factory.

Design performance data

- Cooling capacity (kW): ……

- Unit power input (kW): ……

- Full load energy efficiency, EER (kW/kW): ……

- Eurovent Class ………

- Part load energy efficiency, ESEER (kW/kW): ……

- Heating capacity (kW): .....

- Full load energy efficiency, COP (kW/kW): ……

- Eurovent Class ………

- Part load energy efficiency, SCOP (kW/kW): ……

- SEER 12/7°C Comfort low temp:….

- SEER 23/18°C Comfort medium temp:….

- SEPR 12/7°C Process high temp:….

- Evaporator entering/leaving water temperature (°C): … /

- Fluid type: …….

- Fluid flow rate (l/s): ……

- Evaporator pressure drops (kPa): ……

- Condenser entering/leaving water temperature (°C):

- Fluid type: R-1234ze (GWP < 1)

- Fluid flow rate (l/s): ……

- Condenser pressure drops (kPa): ……

- Sound power level at full load (dB(A)): ……

- Dimensions, length x depth x height (mm): … x … x

Performance shall be declared in accordance with EN14511-3:2013 and certified by Eurovent up to 1500 kW.

Unit sound power level at 50% of the load shall be at minimum 8 dB(A) lower than sound at full load.

Sound power level at 75%, 50% and 25% load (at typical ESEER conditions) shall be declared by the manufacturer.

The unit shall be capable of starting with 13°C entering water temperature to the condenser with condenser head pressure control option. The unit shall be capable of starting with 35°C entering water temperature to the evaporator.

The machine shall operate with condenser leaving water temperature up to 55 °C.

Frame

- Machine frame shall include heat exchangers and compressors in a self-supporting structure

- Electrical panel doors shall be accessible by 1/4-turn screws

Compressor

- Unit shall have semi-hermetic twin-screw compressors with internal relief valve and check valve to avoid reverse rotation on shut down

- Each compressor shall be equipped with a discharge shut-off valve

- The discharge shall also be equipped with a muffler to reduce discharge gas pulsations

- Compressor bearings shall be designed for minimum 73000 hours at maximum operating conditions

- Capacity control shall be provided by an inverter motor acting in combination with slide valve

- Compressor capacity control shall be step-less from 100% to 20% load

- Compressor shall start in unloaded condition

- Motor shall be cooled by suction gas and protected through a dedicated electronic board against the following: thermal overload by internal winding temperature sensors, electrical overload and short circuit by dedicated fuses (one per phase), reverse rotation, loss of phase, under-voltage and power supply failure

- Lubrication oil system shall include pre-filter and external filter capable of filtration to 5 microns

- The oil filter line shall be equipped with service shut off valves for easy filter replacement

- The oil separator, shall be integrated in the condenser design and shall not require oil pump

- The oil separator shall include an oil level safety switch.

Evaporator

- Unit shall be equipped with a single flooded evaporator

- Evaporator shall be manufactured by the chiller manufacturer

- Evaporator shall be tested and stamped in accordance with the European directive for pressurized equipment 97/23/EC

- The maximum refrigerant-side operating pressure will be 2100 kPa, and the maximum waterside pressure will be 1000 kPa (2100kPa as an option)

- The evaporator shall be mechanically cleanable, shell and-tube type with removable heads

- Tubes shall be internally and externally grooved, seamless-copper, and shall be rolled into tube sheets

- Shell shall be insulated with 19 mm closed-cell foam with a maximum K factor of 0.28. Evaporator thermal insulation shall be factory fitted

- The evaporator shall have a drain and vent in each head

- Chiller shall have only one water inlet & outlet connection with Victaulic couplings to avoid vibrations transmission and to accommodate minor pipework misalignment (Victaulic adapter kit shall be available on demand)

- The evaporator shall incorporate an indirect refrigerant level control system (based on the continuous measurement of the approach value) to ensure optimum heat transfer performance under all load conditions

- Design shall incorporate either 1 or 2 independent refrigerant circuits

- Evaporator shall be fitted with electronic auto setting water flow switch. Paddle switches or differential pressure switches shall not be acceptable.

Condenser

- Unit shall be equipped with a single condenser

- Condenser shall be manufactured by the chiller manufacturer

- Condenser shall be tested and stamped in accordance with the European directive for pressurized equipment 97/23/EC

- Single pass or 2-passes design shall be possible

- The maximum refrigerant-side operating pressure will be 2100 kPa, and the maximum waterside pressure will be 1000 kPa (2100kPa as an option)

- The condenser shall be mechanically cleanable shell and-tube type with removable heads

- Tubes shall be internally and externally grooved, seamless-copper, and shall be rolled into tube sheets

- The condenser shall have a drain and vent in each head

- Chiller shall have only one water inlet & outlet connection with Victaulic couplings to avoid vibrations transmission and to accommodate minor pipework misalignment (Victaulic adapter kit shall be available on demand)

- Design shall incorporate either 1 or 2 independent refrigerant circuits plus the oil separator.

Refrigerant circuit

- Refrigerant circuit components shall include: compressor, oil separator, high and low side pressure relief devices, economizer, filter driers, moisture indicating sight glasses, long stroke electronic expansion device, and complete operating charge of both refrigerant R-1234ze and compressor oil.

(Carrier option 92) A compressor suction and discharge line shut off valve, an evaporator inlet valve and economizer line valve, shall be mounted to isolate all main components (filter drier, oil filter, expansion device and compressor) and allow refrigerant to be safely stored during service operation

(Carrier option 257) Evaporator and refrigerant gas suction line shall be acoustically insulated.

Power control box

- Unit shall operate at 400 Volts (+/- 10%), 3-phases, 50 Hertz power supply without neutral

- Unit shall be designed for simplified connection on TN(s) networks

- Control circuit voltage shall be 24 V maximum, supplied by a factory-installed transformer

- Unit shall be supplied with factory-installed main circuit breaker/isolator

- Unit shall have single point power connection (Carrier option 81 for sizes 1150/1710)

- The inverter driven compressor motors start up current shall be less than the full load operating current

- Displacement power factor at full load should be higher than 0.97

- Power control box is powered painted with hinged and gasket sealed doors and is protected to IP23.

Controls

- Unit control shall include as a minimum: microprocessor with non-volatile memory, picture guided unit/operator interface, the LOCAL/OFF/REMOTE/CCN selector and a 7 inches colored touch-screen display with multiple language capability

- Pressure sensors shall be installed to measure suction, discharge, and oil pressure

- Temperature probes shall be installed to read cooler/condenser entering and leaving temperatures.

- Capacity to add up to two (2) user e-mail addresses for the automatic submission of fault reports.

- (Carrier option 158A) Unit control shall include as a minimum: microprocessor with non-volatile memory, picture guided unit/operator interface, the LOCAL/OFF/REMOTE/CCN selector and a 7 inches colored touch-screen display with multiple language capability

Diagnosis

- Control interface shall be capable of displaying set points, system status including temperatures, pressures, current for each compressor, run time and percent loading

- Control interface shall perform trending of up to 10 preselected variables

- Control system shall allow a quick test of all machine elements to verify the correct operation of every switch, circuit breaker, contactor etc. before the chiller is started

- In case of alarm, control system shall send an email to specific mail box set by user during machine commissioning

- Control shall have black box function which permit to store data set of 20 variables with interval of 5 seconds, during 14 minutes before the alarm and 1 minute following the alarm event. The black box recording capability shall permit recording for 20 events and once the threshold is reached new data shall over-write the oldest ones.

Safeties

Control system shall provide the unit with protection against the following:

- Reverse rotation

- Low chilled water temperature

- Low oil pressure (per compressor)

- Current imbalance

- Compressor thermal overload

- High pressure (with automatic compressor unloading in case of excessive condensing temperature)

- Electrical overload and short circuit

- Loss of phase, under-voltage and power supply failure

Control shall provide separate general alert (minor incident) and alarm (circuit down) remote indication