Product specifications in italic shall be considered as key requirements.

SYSTEM DESCRIPTION

Factory assembled, air to water split type heat pump utilizing DC inverter Twin-Rotary compressor  with Pulse Amplitude Modulation (PAM) and Pulse Width Modulation (PWM) and variable speed fans. The unit shall include all necessary wiring, piping, charge of R410A refrigerant, microprocessor controls and user display.

QUALITY ASSURANCE

Unit shall be rated in accordance with EN14511-3 Standard, latest revision and unit performances shall be certified by independent Eurovent certification body. Unit without independent Eurovent certification shall be excluded.

Unit construction shall comply with European directives:

- Commission Regulation (EU) N° 813/2013 implementing Directive 2009/125/EC of the European Parliament and of the Council with regard to Eco-design requirements for space heaters and combination heaters

- Commission regulation (EU) N°327/2011 implementing Directive 2009/125/EC with regards to Eco-design requirements for industrial fans.

- Low voltage directive 2006/95/EC, modified.

- Electromagnetic compatibility directive 2004/108/EC, modified, and the applicable recommendations of European standards.

- 2011//65/CE

Unit shall be manufactured in European country in a facility registered to ISO 9001 Manufacturing Quality Standard and to ISO 14001 Environmental Management System. Unit shall be tested at the factory.

DESIGN PERFORMANCE DATA

- Cooling Capacity (kW): ………..*

- Heating Capacity (kW): ………..*

- SCOP according to EN14825: 3 2013 (kWh / kWh): ………..(average climate zone and water temperature  30οC/35oC)

- SCOP according to EN14825: 3 2013 (kWh / kWh): ………..(average climate zone and water temperature  47οC/55oC)

- Refrigerant type: R-410A

- Compressor type: DC inverter Twin-Rotary

- Evaporator Pressure Drop (kPa): ......

- Sound power level at full load (dB(A)): ……

- Sound pressure level 4m (dB (A)): …… ………..(for water temperature  47οC/55oC)

- Refrigerant amount : ...... .. kg (. ... Kg / kW)

- Dimensions, length x depth x height (mm): …… x …… x ……

- Unit operating weight: ….. kg

*Operating Conditions:

- Cold water inlet / outlet temperature (° C): ……..

- Hot water inlet / outlet temperature (° C): ……..

- Ambient temperature (° C) in cooling mode: ……..οC DB

- Ambient temperature (° C) in heating mode: ……..οC DB (RH 87%)

MAIN FEATURES

The following features shall be available and factory installed as part of the unit’s control algorithm.

- Wide operating range in both heating and cooling mode offering high performance in a wide temperature range.

- DC inverter twin-rotary compressors with Pulse Amplitude Modulation (PAM) and Pulse Width Modulation (PWM) for enhanced reliability, low energy consumption and smooth vibration-free operation under all operating conditions.

- Variable-speed fans with an innovative patented fan blade shape ensure improved air distribution at exceptionally low noise levels

- Pre-set or customized selection of the appropriate climate curve for stable output capacity to match the heat load.

- Output to link and integrate the unit with existing heat sources or a back-up heating source (single or dual-energy approach) for increased savings and optimum comfort all year round.

- The system shall be able to control two independent comfort zones with a two-zone kit added to the main comfort module.

- Leaving water temperature shall be up to 60°C for radiator and domestic hot water applications.

-  Back-up heating shall be available to support the heating system either electrical (single-energy applications) or gas boiler (dual-energy applications).

-  Comfort shall be ensured via the user interface and the possibility of integrating two leaving water temperature zones.

- OUTDOOR UNIT

UNIT CONSTRUCTION

The outdoor unit shall have exceptional small foot-print and  provide easy access to all internal components by simply removing three screws in order to remove the complete front panel to access the refrigerant piping connections, control box and electrical connections, as well as the compressor and other key parts.

The unit shall have pre-punched holes in the cabinet panels to permit cable exit on the side, front or rear, offering various power cable outlet options.

The color of the chassis shall be beige.

COMPRESSOR ASSEMBLY

The unit shall be equipped with DC inverter Twin-Rotary compressor. Advanced technology DC inverter twin-rotary compressor shall provide maximum energy-efficiency with high capacity available at peak conditions and optimised efficiency at low and mid compressor speeds. The heat pump DC inverter system shall use Intelligent Power Drive Unit (IPDU) hybrid inverter technology, combining two electronic management logics: Pulse Amplitude Modulation (PAM) and Pulse Width Modulation (PWM) for optimised compressor operation in all conditions, minimised temperature fluctuations, and providing perfect individual comfort control with significantly reduced energy consumption:

- PAM: pulse amplitude modulation of the direct current shall control the compressor at maximum load conditions (start-up and peak load), increasing the voltage at fixed frequency. The compressor shall work at high speed to rapidly achieve the desired temperature.

- PWM: pulse width modulation of the direct current shall control the compressor at partial load conditions, adjusting the frequency at fixed voltage. The compressor speed shall be fine-tuned and the system shall provide high-level comfort (no temperature fluctuations) at exceptionally efficient working conditions.

The pulse modulation valve shall be a bi-flow electronic expansion device which optimizes the refrigerant amount in the circuit and the superheat, preventing refrigerant migration back into the compressor. This device shall further enhance high system performance and reliability.

Compressor frequency shall be increased continuously up to the maximum level. This shall ensure that there are no current draw peaks in the start-up phase and safe connection to a single phase power supply even in large-capacity systems (for single power connection units).

The two rotary compression cylinders, shall offset from each other by 180°, and the DC brushless motor  with the shaft in perfect balance shall ensure reduced vibration and noise, even at very low operating speeds. This shall obtain an extremely wide range between minimum and maximum capacity with continuous operation, guaranteeing that the system shall be always optimised and shall provide maximum comfort at exceptionally high efficiency levels. Twin-rotary cylinders, low vibrations and low load to the shaft shall ensure highest compressor reliability and a long trouble-free operating life.

All DC brushless twin-rotary compressors shall be equipped with crankcase heaters as standard.

A standard double compressor shield for acoustic insulation further shall reduce noise levels.

AIR HEAT EXCHANGER

The unit shall be equipped with vertical condenser coils. Coils shall be air-cooled with copper tube aluminium fins heat exchanger (Cu/Al)

FANS

The unit shall be equipped with Brushless DC motor for increased fan performance and reliability and with variable speed 3 blades fan(s) made of composite materials with an innovative patented fan blade shape to ensure improved air distribution at exceptionally low noise levels .

REFRIGERANT

The unit shall work with R410A refrigerant

REFRIGERANT CIRCUIT

The unit shall have electronic system management with several sensors placed in key positions in the refrigerant circuit electronically detect the operational system status. Two micro-controllers shall receive the input from the sensors, manage them using advanced control algorithms and optimize the refrigerant flow and the functioning of all core components - the compressor, fan motors and the pulse modulation valve.

The pulse modulation valve shall be a bi-flow electronic expansion device which optimizes the refrigerant amount in the circuit and the superheat, preventing refrigerant migration back into the compressor. This device shall further enhance high system performance and reliability.

ELECTRIC FEATURES

The outdoor unit shall operate on 230V, 1-phase, 50Hz +/-10% for sizes up to 11,5KW and on 400V, 3-phase, 50Hz +/-10% for sizes 12-15 KW.

OPERATING CHARACTERISTICS

Unit shall be capable to operate at ambient temperatures from -20°C to 30°C in heating mode and from  0°C to 46°C in cooling mode. Minimum / maximum leaving water temperature shall be 20°C / 60°C and 4°C / 18°C in heating / cooling mode respectively.

- INDOOR UNIT

The indoor unit shall be compact and provide energy savings and indoor comfort. The indoor unit shall be equipped with the following elements:

- Electric heaters (not for models M0): 3KW 1ph., 6KW 1ph., 6KW 3ph., 9KW 3ph.

- Variable speed Circulator

- Expansion tank 8 lt

- Buffer Tank 10 lt

- User interface mounted on the unit

- Manometer

- Control Box

- Main Board

- Terminal Block

- Water temperature sensors

- Flow switch

- Water heat exchanger

- Refrigerant sensor

- Air purge valve

- Drain valve

PHYSICAL DATA

The indoor unit shall meet the below characteristics

- Sound power level at full load (dB(A)): ……

- Dimensions, length x depth x height (mm): 450 x 330 x 800

- Unit operating weight: ….. kg

- Chassis Color: White

- Circulator: Variable speed circulator

TWO ZONE KIT

The two-zone kit, shall separate two types of terminal units or two independent comfort zones and can be closely monitored. Domestic hot water production shall be easily managed and shall be able to be interfaced with thermal solar panels.

The 2nd zone management kit shall include a hydronic disconnection collector, the necessary circulating pumps and modulating valves.

When installed together with the domestic hot water tank, the two-zone kit shall integrate all accessories, such as the diverting valve and T-connection.

The 2nd zone kit, shall be equipped with the following elements additionally to indoor unit:

- Water temperature sensors

- Water pump for zone 1

- Water pump for zone 2

- 3 way valve and actuator

- Collector

- Pressure switch

- Drain valve

- Control box

- Electronic board

- Terminal block

The 2nd zone kit shall have the following dimensions in order to be exactly match with the indoor unit:

length x depth x height (mm): 450 x 330 x 485

WATER HEAT EXCHANGER

The unit shall be equipped with high efficiency brazed plate heat exchanger, made of AISI 316L stainless steel.

CONTROL PANEL – USER INTERFACE

The controller shall be specifically developed for inverter units, and shall incorporate new control algorithms. It shall feature customised or pre-defined climate curves, domestic hot water control, a night-time noise reduction function, a defrost/alarm output signal, management of an external heat source, a pump block prevention function, freeze protection and compressor operation management.

The programmable thermostat shall be equipped with easy-to-read LCD screen. It shall provide enhanced control capability for maximised performance, reliability and indoor comfort and shall have extended programming features such as weekly scheduling and dehumidifier/ humidifier signals. The following information/ programming features shall be available through the programmable thermostat:

- Manual output tests

- Operating mode requested by the unit’s control board: off, stand by, cooling, heating, freeze protection, defrost, high temperature protection, timeguard, system fail.

- Critical temperatures: leaving water temperature, refrigerant temperature, tank temperature, domestic hot water temperature.

- Operating time of compressor and water pump.

- Current unit’s alarm and alarm history.

- Maximum compressor’s frequency

- Requested compressor’s frequency

- Real compressor’s frequency

- Requested leaving water setpoint temperature / real leaving water setpoint temperature

- Selection among 6 pre-defined compensation curves for heating mode and  between 2 for cooling mode

- Customized compensation curves for heating and cooling mode.

- Customization for electric heaters / external heat source control.

- DHW disinfection schedule (if DWH is managed by system control).