General Description

Modular, ultra-slim (maximum height 400 mm) ventilation unit with option to include built-in automated control designed to meet all energy efficiency related requirements as dictated by Ecodesign Directive 2009/125/CE, to be available in several assemblies: single flow, aligned dual-flow and adjacent dual-flow. Unit to be available in a minimum of three (3) configurations to match all installation sites; the horizontal ceiling-mounted (bottom access), the horizontal floor-mounted (top access) and the vertical wall-mounted configuration (front access). Maximum unit casing width should not exceed 1,880 mm to minimise unit footprint; nominal airflow range: 1,000 to 6,000 m3/h.

| Ecodesign Directive 2009/125/CE Requirements for Unidirectional Ventilation Units |  |  |
| --- | --- | --- |
| Min. Fan Motor Assembly (FMA) Efficiency % | Abs. Power ≤ 30 kW | 6.2 x ln(P) + 42 |
|  | Abs. Power > 30 kW | 63.10 % |
| Max. Specific Fan Power (SFPint) | 230 W/m3s-1 |  |

| Ecodesign Directive 2009/125/CE Requirements for Bidirectional Ventilation Units |  |  |
| --- | --- | --- |
| Non-Heat Recovery Units | Unacceptable |  |
| Heat Recovery Systems without Heat Transfer Fluid (e.g. plate heat exchangers, rotary heat wheels) | Minimum Efficiency (h) of Recuperator | 73% |
|  | Bonus (E) (should Recuperator Efficiency exceed minimum requirements) | (h – 0.73) x 3,000 |
|  | Max. Specific Fan Power (SFPint) [W/m3s-1] Flow Rate (Q) < 7,200 m3/h | 1,100 + E – 300 x (Q/2) – F |
|  | Max. Specific Fan Power (SFPint) [W/m3s-1] Flow Rate (Q) ≥ 7,200 m3/h | 800 + E - F |

Product to be suitable for all applications that require central ventilation. Unit should be ideal for compact installations in narrow spaces (e.g. ceilings, closets, basements etc.); unit should only be fit for indoor installation. Typical applications for this product range include but are not limited to: administrative buildings and offices, educational facilities, hotels, restaurants, shopping centres, various healthcare facilities as well as collective housing premises.

Products to be ISO 9001 and ISO 14001 certified.

| Minimum Acceptable AHU Specifications |  |
| --- | --- |
| Casing Mechanical Strength | D2 |
| Casing Air Leakage (-/+ Pressure) | L2 |
| Filter Bypass Leakage | F9 |
| Thermal Transmittance | T3 |
| Thermal Bridging Factor | TB2 |

Criteria

Casing Mechanical Strength

Casing Mechanical Strength is determined using two (2) different test criteria.

- Relative Deflection [in mm x m-1]: Measured deflection of posts and panels under normal design conditions. 
EN 1886 dictates that relative deflection tests are to be carried out at +1,500 Pa/-1,500 Pa.

- Mechanical Resistance [with no permanent deformation]: Measured against maximal fan pressure. 
EN 1886 dictates that mechanical resistance tests are to be carried out at +2,500 Pa/-2,500 Pa.

| Casing Mechanical Strength Classes (EN 1886) |  |  |  |
| --- | --- | --- | --- |
| Class | Maximum Relative Deflection [mm x m-1] | Mechanical Resistance at Maximum Fan Pressure [no permanent deformation] | Quality |
| D1 | 4 | Yes | + |
| D2 | 10 | Yes | ↑ |
| D3 | - | Yes | - |

Casing Air Leakage

Depending on AHU arrangement and nominal operating pressures, air leakage is measured at the following test conditions:

- All sections tested at -400 Pa, should the unit operate on negative pressure.

- Positive pressure sections tested at +700 Pa, should the operating pressure at fan exit be greater than +250 Pa. Should the operating pressure be greater than 700 Pa, positive pressure sections are tested under actual pressure conditions. All remaining sections tested at -400 Pa.

| Air Leakage Classes (EN 1886) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Class | Maximum Leakage at – 400 Pa (l x s-1 x m-2) | Maximum Leakage at + 700 Pa (l x s-1 x m-2) | Maximum Filter Class (EN 779) | Quality |
| L1 | 0.15 | 0.22 | Greater than F9 | + |
| L2 | 0.44 | 0.63 | F8-F9 | ↑ |
| L3 | 1.32 | 1.90 | G1-F7 | - |

Filter Bypass Leakage

Filter bypass leakage refers to the total amount of unfiltered air. The unfiltered air is the sum of:

- Air that bypasses the filter.

- Air leaking through the casing of the AHU under negative pressure conditions.

| Filter Bypass Leakage Classes (EN 1886) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Filter Class | G1 – G4 | F5 | F6 | F7 | F8 | F9 |
| Bypass Leakage % | - | 6 | 4 | 2 | 1 | 0.5 |

Thermal Transmittance

Thermal transmittance is determined based on the average heat transfer coefficient U of the tested AHU section. AHU sections are allocated to a thermal transmittance class based on the derived U-value (please refer to the table given below).

| Thermal Transmittance Classes (EN 1886) |  |  |
| --- | --- | --- |
| Class | Heat Transfer Coefficient U [W x m-2 x K-1] | Quality |
| T1 | U < 0.5 | + |
| T2 | 0.5 < U < 1.0 | ↑ |
| T3 | 1.0 < U < 1.4 |  |
| T4 | 1.4 < U < 2.0 |  |
| T5 | - | - |

Thermal Bridging Factor

The heat transfer factor kb is calculated by dividing the least temperature difference between mean internal air temperature and maximum external surface temperature by the temperature difference between internal and external air streams. The measured value is allocated to a thermal bridging factor class (please refer to the table given below) and is used to indicate the probability of surface condensation occurring on the examined AHU arrangement. A higher thermal bridging factor implies a lower condensation occurrence probability.

| Thermal Bridging Classes (EN 1886) |  |  |
| --- | --- | --- |
| Class | Heat Transfer Factor kb [W x m-2 x K-1] | Quality |
| TB1 | 0.75 < kb < 1.00 | + |
| TB2 | 0.60 < kb < 0.75 | ↑ |
| TB3 | 0.45 < kb < 0.60 |  |
| TB4 | 0.30 < kb < 0.45 |  |
| TB5 | - | - |

Unit Specification

Unit technical characteristics:

- Supply airflow: …. m3/h

- Extraction airflow: …. m3/h

- External static pressure, supply airflow: …. Pa

- External static pressure, extraction airflow: …. Pa

- Cooling Coil Capacity: …. kW

- Maximum coil velocity: …. m/s

Component Description

Casing

- AHU to be made of self-supporting, double-skin panels with no internal frame (thickness 8/10 mm) of steel metal sheets, galvanised on both sides to ensure a robust and corrosion-resistant envelope.

- Outer AHU envelope sheet to be pre-coated in grey RAL 7035 to enhance durability in corrosive conditions.

- Unit to be insulated with no less than 25 mm thick mineral wool insulation. Insulation material density should be at least 24 kg/m3. Envelope insulation ensures the absence of thermal bridges between the internal and external surfaces of the AHU, minimizing the potential for condensation and unwanted heat transfer.

- Minimum acceptable Euro Class Fire Classification: A1.

- No AHU component should exceed the following limitations: casing height of 400 mm, casing length of 1,400 mm and casing width of 1,880 mm. This is to meet even the most demanding space limitations.

- Unit to be suitable for indoor installation only; service side (fluid and electric connections) to be configurable
(options: either left- or right- hand side, depending on customer preference and installation-specific limitations).

Fans

- Plug Fan type, direct drive Fan Motor Assembly (FMA).

- FMA to be equipped with either AC motors [Comefri NPL 280] (frequency inverter option available) or EC motors
(electronically commutated motor with built-in variable speed control) [EBM PAPST K3G 280].

- Available fans and motors to be selected based on efficiency and acoustic performance.

- Depending on fan operating point, FMAs are to contain either one (1) or two (2) fans.

- Aluminium turbine fan option should be available.

- Option to include electric switch (mounted and wired) and/or frequency inverter (1~230V or 3~400V).

- Fan to be fastened directly on AHU casing; vibration attenuators to be placed between AHU casing and casing support.

Hydraulic & Direct Expansion Coils

- A range of hydraulic and direct expansion (DX) coils should be available. All coils to be made of copper tubes mechanically expanded into aluminium fins (0.1 mm thick) achieving high thermal efficiency. Available coil fin spacing options: 1.8 mm, 2.1 mm and 2.5 mm.

- Coil sizes: Hydraulic cooling coils should have up to six (6) rows, hydraulic heating coils up to four (4) rows and DX coils of either three (3) or six (6) rows.

- Hydraulic coils to be fully drainable with drain holes in place.

- All cooling coil condensate drain pans to be made of stainless steel (Option to include SS 304L drain pan with half an inch (½’’) connection).

- Galvanized droplet eliminator to be available for all hydraulic cooling and DX coils.

- Optional frost protection thermostat with automatic reset to be available for all hydraulic coils.

- Vertical coil mounting to be available for vertical unit configuration.

- Minimum operating limit requirements for hydraulic cooling coils and DX coils:

  - Maximum Air Velocity: 3.10 m/s.

  - Maximum Condensation: 8 gkg-1 of dry air.

  - Supply Air Temperature ≥ 10 oC.

Electric Heaters

- To be made of shielded resistors in scrolled finned pipes.

- Two-stage electric heaters available to be fitted in main AHU casing.

- Option for two- and four- stage electric heaters to be added to AHU arrangement (additional box) if required.

- Two (2) high-limit safety thermostats; one (1) automatic and one (1) with manual reset.

- Anti-radiation screen to be available, depending on upstream and downstream components.

- Maximum air temperature of 60 oC.

Filters

- Filter cell with universal dimensions should be available to simplify filter replacement.

- Two-stage filters should be available; three filtration stages should be possible per airflow.

- Available pleated filters: G4, M5, F7 and F9 HPE.

- Available short bag filters: M6 to F7 efficiency class.

- Available rigid bag filters: M6 to F9 efficiency class.

- Pressure tappings to be fitted on each filter section.

- List of options that should be available:

  - Liquid manometers

  - Differential pressure switches

  - Set of replacement filters

Dampers & Mixing Sections

- Class 1 dampers (EN 1751) by default; option to add Class 3 dampers to AHU arrangement.

- Standard damper thickness and height of at least 110 mm and 310 mm respectively.

- Option to add servo-motor to dampers.

- Two- and three- way mixing sections available.

Criteria

Leakage Classification (EN 1751) is used to determine the degree to which air leaks through the damper when a differential pressure of 100 Pa is applied to the component.

| Leakage Classes (EN 1751) |  |  |
| --- | --- | --- |
| Class | Leakage Factor [m3/s per m2 of damper area] | Quality |
| Class 0 | - | - |
| Class 1 | 0.2 | ↓ |
| Class 2 | 0.04 |  |
| Class 3 | 0.008 |  |
| Class 4 | 0.0015 | + |

Heat recovery

- Plate heat exchanger to be available for bidirectional ventilation units (side-by-side configuration).

- Component efficiency to be in line with Ecodesign Directive 2009/125/CE minimum requirements.

- Air by-pass option to be available on damper-equipped plate heat exchangers to allow for icing control in low ambient temperatures and free cooling operation.

Control

Option to include built-in automated control. Minimum required automated control features given below:

- Factory fitted Plug & Play control system (when EC fans are selected).

- Pre-wired programmer mounted inside fan section.

- 3-Ph 400V power supply + Earth.

- Main disconnect switch.

- 24V transformer for control circuit.

- Quick connection blocks for external components and options (e.g. probes, actuators, etc.).

- Standard Human - Machine Interface (HMI).

- Sensor values display (e.g. temperature, volumetric airflow rate, pressure).

- AHU status display (e.g. unit stopped, cooling or heating operation).

- Set point values display (e.g. temperature, volumetric airflow rate, pressure).

- Alarms display (including recorded alarm history).

- Clock settings.

- Remote controller (6 m wire supplied).

Scheduling Options

Minimum required scheduling features given below:

- Programming settings: daily/weekly/annual; summer/winter time management.

- Comfort T°: AHU runs at Comfort T° set point.

- Eco T°: AHU runs at Eco T° set point.

- Comfort Airflow: AHU runs at Comfort Airflow set point (supply and exhaust airflows may not be equal).

- Eco Airflow: AHU runs at Eco Airflow set point. (supply and exhaust airflows may not be equal).

- Comfort Pressure: AHU runs at Comfort Duct Pressure (supply airflow).

- Eco Pressure: AHU runs at Eco Duct Pressure (supply airflow).

- Night Cooling: should outdoor temperature be within desired temperature range, unit operates to reach
Night Cooling set point.

- Eco Recirculation: two- or three-way mixing damper open (% of opening adjustable).

- Morning Heating: allows for a quick heating of the building.

Additional Features

- Zoning function should be available with the capacity to manage at least up to eight (8) units. System features listed below:

  - Automatic unit operational rotation on a weekly basis.

  - Capacity to automatically operate several units in cases of high building thermal/cooling load.

  - Max. acceptable distance between first and last connected unit at least 500 m.

  - Max. acceptable distance between HMI and connected unit at least 50 m.

  - Humidifier Contact: allowing for an autonomous humidifier to work when the unit is in operation.

  - External ON/OFF contacts.

  - Fire detection contact.

  - Electric heater relief contact.

  - BMS COMM: Connection to all major protocols (e.g. LON, KNX, ModBus, Bacnet).

- In-room remote controller (final user interface). System required features listed below:

  - Remote Controller should be connected to unit using a Licy 4 x 0.75 shielded cable.

  - Maximum distance between unit and remote controller should be no greater than 200 m.

  - Integrated room temperature sensor should be available.

  - Capacity to change temperature set point using remote. Minimum and maximum set points may be limited using unit main remote.

  - Capacity to change airflow set point using remote (e.g. standby – low speed – high speed).

  - During clock programming (Eco or Standby), the in-room remote should be able force the unit to operate in comfort mode. The unit then should automatically switch back to clock programming on the next time slot.

- Semi Plug & Play control system. System features listed below:

  - External components to be wired to control box on-site (pressure sensors, valve actuators, additional electric box for electric heaters, etc.).

  - Electric heater regulation box, valves, motors and pressure sensors to be fitted out of casing.

- Without control system:

  - Installer/Customer is to provide his own control system.

Accessories

Unit should also be able to be equipped with the following:

- Two-channel mixing box: Minimum of three (3) air flow positions available.

- 3-way mixing box.

- Angled or straight plenum.

- Sound attenuator.