General Description

Autonomous, Plug & Play, dual-flow ventilation unit equipped with a highly efficient heat recovery section, plug fans with high performance EC motors as well as built-in automation control for operation optimisation designed to meet all energy efficiency related requirements as dictated by Ecodesign Directive 2009/125/CE. Ventilation unit to be supplied ready to use, pre-wired and factory pre-programmed. Unit to be supplied with a remote controller.

| Ecodesign Directive 2009/125/CE Requirements for Bidirectional Ventilation Units |  |  |
| --- | --- | --- |
| Non-Heat Recovery Units | Unacceptable |  |
| Heat Recovery Systems without Heat Transfer Fluid (e.gr plate heat exchangers, rotary heat wheels) | Minimum Efficiency (h) of Recuperator | 73% |
|  | Bonus (E) (should Recuperator Efficiency exceed minimum requirements) | (h – 0.73) x 3,000 |
|  | Max. Specific Fan Power (SFPint) [W/m3s-1] Flow Rate (Q) < 7,200 m3/h | 1,100 + E – 300 x (Q/2) – F |
|  | Max. Specific Fan Power (SFPint) [W/m3s-1] Flow Rate (Q) ≥ 7,200 m3/h | 800 + E - F |
| Heat Recovery Systems with Heat Recovery Fluid (e.g. run-around coils, heat pipes) | Minimum Efficiency (h) of Recuperator | 68% |
|  | Bonus (E) (should Recuperator Efficiency exceed minimum requirements) | (h – 0.68) x 3,000 |
|  | Max. Specific Fan Power (SFPint) [W/m3s-1] Flow Rate (Q) < 7,200 m3/h | 1,600 + E – 300 x (Q/2) – F |
|  | Max. Specific Fan Power (SFPint) [W/m3s-1] Flow Rate (Q) ≥ 7,200 m3/h | 1,300 + E - F |

Air Handling Unit (AHU) should be able to condition fresh air using, on average, 80% less energy than conventional non-heat recovery AHUs. Product should be suitable for all applications that require central ventilation. Typical applications for this product range include but are not limited to: administrative buildings and offices, educational facilities such as libraries and community centres, hotels, restaurants, shopping centres, nursing homes and various other healthcare facilities as well as collective housing premises.

Product to be ISO 9001 and Eurovent Class A+ certified across entire range.

| Minimum Acceptable AHU Specifications |  |
| --- | --- |
| Casing Mechanical Strength | D2 |
| Casing Air Leakage (-/+ Pressure) | L2 |
| Filter Bypass Leakage | F9 |
| Thermal Transmittance | T3 |
| Thermal Bridging Factor | TB2 |

Criteria

Casing Mechanical Strength

Casing Mechanical Strength is determined using two (2) different test criteria.

- Relative Deflection [in mm x m-1]: Measured deflection of posts and panels under normal design conditions. 
EN 1886 dictates that relative deflection tests are to be carried out at +1,500 Pa/-1,500 Pa.

- Mechanical Resistance [with no permanent deformation]: Measured against maximal fan pressure. 
EN 1886 dictates that mechanical resistance tests are to be carried out at +2,500 Pa/-2,500 Pa.

| Casing Mechanical Strength Classes (EN 1886) |  |  |  |
| --- | --- | --- | --- |
| Class | Maximum Relative Deflection [mm x m-1] | Mechanical Resistance at Maximum Fan Pressure [no permanent deformation] | Quality |
| D1 | 4 | Yes | + |
| D2 | 10 | Yes | ↑ |
| D3 | - | Yes | - |

Casing Air Leakage

Depending on AHU arrangement and nominal operating pressures, air leakage is measured at the following test conditions:

- All sections tested at -400 Pa, should the unit operate on negative pressure.

- Positive pressure sections tested at +700 Pa, should the operating pressure at fan exit be greater than +250 Pa. Should the operating pressure be greater than 700 Pa, positive pressure sections are tested under actual pressure conditions. All remaining sections tested at -400 Pa.

| Air Leakage Classes (EN 1886) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Class | Maximum Leakage at – 400 Pa (l x s-1 x m-2) | Maximum Leakage at + 700 Pa (l x s-1 x m-2) | Maximum Filter Class (EN 779) | Quality |
| L1 | 0.15 | 0.22 | Greater than F9 | + |
| L2 | 0.44 | 0.63 | F8-F9 | ↑ |
| L3 | 1.32 | 1.90 | G1-F7 | - |

Filter Bypass Leakage

Filter bypass leakage refers to the total amount of unfiltered air. The unfiltered air is the sum of:

- Air that bypasses the filter.

- Air leaking through the casing of the AHU under negative pressure conditions.

| Filter Bypass Leakage Classes (EN 1886) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Filter Class | G1 – G4 | F5 | F6 | F7 | F8 | F9 |
| Bypass Leakage % | - | 6 | 4 | 2 | 1 | 0.5 |

Thermal Transmittance

Thermal transmittance is determined based on the average heat transfer coefficient U of the tested AHU section. AHU sections are allocated to a thermal transmittance class based on the derived U-value (please refer to the table given below).

| Thermal Transmittance Classes (EN 1886) |  |  |
| --- | --- | --- |
| Class | Heat Transfer Coefficient U [W x m-2 x K-1] | Quality |
| T1 | U < 0.5 | + |
| T2 | 0.5 < U < 1.0 | ↑ |
| T3 | 1.0 < U < 1.4 |  |
| T4 | 1.4 < U < 2.0 |  |
| T5 | - | - |

Thermal Bridging Factor

The heat transfer factor kb is calculated by dividing the least temperature difference between mean internal air temperature and maximum external surface temperature by the temperature difference between internal and external air streams. The measured value is allocated to a thermal bridging factor class (please refer to the table given below) and is used to indicate the probability of surface condensation occurring on the examined AHU arrangement. A higher thermal bridging factor implies a lower condensation occurrence probability.

| Thermal Bridging Classes (EN 1886) |  |  |
| --- | --- | --- |
| Class | Heat Transfer Factor kb [W x m-2 x K-1] | Quality |
| TB1 | 0.75 < kb < 1.00 | + |
| TB2 | 0.60 < kb < 0.75 | ↑ |
| TB3 | 0.45 < kb < 0.60 |  |
| TB4 | 0.30 < kb < 0.45 |  |
| TB5 | - | - |

Unit Specification

Unit technical characteristics:

- Supply airflow: …. m3/h

- Extraction airflow: …. m3/h

- External static pressure, supply airflow: …. Pa

- External static pressure, extraction airflow: …. Pa

- Cooling Coil Capacity: …. kW

- Maximum coil velocity: …. m/s

Component Description

Casing

- AHU to be made of self-supporting, double-skin panels (thickness 8/10 mm) of steel metal sheets, galvanised
(225 g/m2) on both sides to ensure a robust and corrosion-resistant envelope.

- Outer AHU envelope sheet to be pre-coated in grey RAL 7035 to enhance durability in corrosive conditions.

- Unit to be insulated with no less than 50 mm thick mineral wool insulation made of long fibres reinforced with glass fibre cloth (bonded to the insulating mat). Insulation material density should be at least 28 kg/m3.Envelope insulation ensures the absence of thermal bridges between the internal and external surfaces of the AHU, minimizing the potential for condensation and unwanted heat transfer.

- Minimum acceptable Euro Class Fire Classification: A1.

- Corrosion-proof compression seals and EPDM profiled seals to be fitted on all access doors.

- Access and dismantling of all internal elements by wide (lift-off) hinged doors. The dimensions of the hinged doors should be such to allow unobstructed access to all AHU components.

- Sections to be equipped with supporting feet.

- Panel crossings (rubber funnels, pressure tapings, and piping) to be installed during factory-assembly.

Outdoor Installation AHUs

- Units to be equipped with bulged roof (minimum overtaking on both sides: 80 mm).

- AHU openings on fresh air inlet and extracted air outlet sides to be protected by rain-hoods.

- Hydraulic valves to be positioned inside the unit; accessible by door on operating face.

Dampers

- Motorised dampers, either circular or rectangular to be equipped with servo-motor.

- Airfoil blade dampers available as an option.

Filters

- Filters available: M5 HEE, F7 HEE and F9 HEE.

- All filters to be fitted with built-in mechanism designed to ensure leak-tight connection to AHU frame.

- Option to include a combined filter section on fresh air side to maximise protection to components and ensure optimal indoor air quality.

- Filter fouling to be monitored by analogue pressure sensors and displayed on controller.

- Option to include pressure switch controls on each air flow. Pressure switch status displayed on controller.

- Filters to be accessible by door on operating face. Removal and replacement of filters possible.

Coils

- Performance to be measured in accordance with EN 1216 requirements.

- Hydraulic connections to be placed internally (EN 13053 conformity); this is to eliminate any thermal bridging between collectors and panels and to ensure section airtightness.

- Hydraulic coils to be fitted with 2- or 3-way control valves and actuators (0-10V) driven by built-in automated control for precise set point selection.

- Coils to be assembled on slides, designed to be removable on operating side without dismantling the upstream or downstream panels (EN 13053 conformity).

- Coil frames to be made of galvanized steel. Heat exchangers to be made of copper tube and aluminium fins.

- Hydraulic cooling and DX coils to be equipped with stainless steel condensate drain pan allowing no water retention.

- Option to add additional cased hydraulic coils to AHU arrangement.

Electric heaters

- Double-isolation, two-stage electric heaters to be equipped with 2 (two) safety thermostats (one (1) with manual reset and one (1) with automatic reset), internal electric box as well as access door.

- Electric heater resistances to be assembled into a finned coil to ensure uniform heat diffusion.

Fans

- Plug fans driven by an electronically commutated motor (EC motor with built-in variable speed control).

- Fans to be able to maintain an External Static Pressure minimum of 250 Pa.

- Fan mechanical safety in compliance with the recommendations of the EN 1886 standard.

Plates Heat Exchanger

- Counter flow technology plate heat exchangers to be fitted with by-pass damper with no 
cross-contamination between fresh and extracted airflows (leakage < 0.5%).

- Thermodynamic performance of all plate heat exchangers to be certified by Eurovent.

- Heat exchanger plates to be made of aluminium.

- Heat recovery section to be equipped with stainless steel condensate drain pan. Pan design to feature a slope for the concentration of condensates. An evacuation tube on the extraction side to be also fitted for the prompt removal of accumulated water; the placing of the evacuation tube in the direction of the extraction airflow is such to avoid generating unnecessary pressure drop on the supply air side.

- Condensate drain pan to be designed for easy removal and cleaning.

- Air by-pass to be equipped with motorised damper driven by built-in automated control to ensure icing control in low ambient temperatures and free cooling operation.

- Dedicated door offering full access to the exchanger plates, the condensate drain pan and the by-pass damper.

Rotary Heat Exchanger

- Constant speed rotary heat exchanger.

- Option to equip rotary heat exchanger with variable speed control motor (0-10 rpm). Motor driven by built-in automated control to ensure icing control in low ambient temperatures and free cooling operation.

- Thermodynamic performance of all rotary heat exchangers to be certified by Eurovent.

- Rotary wheel exchange media to be made of wavy aluminium for sensible heat transfer.

- Air-tightness between wheel and casing to be realised by nylon gaskets and peripheral brush.

- Dedicated door offering full access to the rotary heat exchanger.

Electrics Box:

- Manufacturing of electrics box to be in accordance with EN 60204 requirements.

- Electrics box power supply (3-Ph 400 V + Earth or 1-Ph 230V + Earth).

- Main disconnect switch available.

- Protection and control of all electric components by circuit breaker and contact switch.

- Factory pre-programmed PLC control.

- Fault summary contact.

- Hand-held cabled micro-terminal.

- Peripheral options and power terminal block.

Accessories

- Flexible sleeves.

- CO2 air quality sensors.

- Mixing section.

- ModBus RTU, LON, KNX, ModBus communication.

- TCP, Bacnet IP, Web Interface.