General Description

R410A horizontal-orientation split-type packaged unit designed for indoor installation, able to deliver conditioned air through a network of ducts suitable for installation with condensing units as a part of a custom-made system. Packaged unit to be designed for optimum performance exceeding the minimum requirements set by EU Regulation 2016/2281
(Lot 21) valid as of January 2018. Unit to be available in two (2) configurations to allow both non-reversible (cooling-only) and reversible heat pump operation. Unit to be able to be equipped with two (2) independent cooling circuits. Product to be equipped with centrifugal fan; direct-driven plug fan equipped with EC motor (electronically commutated motor with built-in variable speed control) option to be available. Unit to feature lightweight construction designed specifically to ensure easy installation and unit maintenance. For maximum adaptability, several unit assemblies shall be available. Product to be Ecodesign 2018 ready, ISO 9001 and ISO 14001 certified.

Unit Specification

Unit technical characteristics:

- Supply airflow: …. m3/h

- Extraction airflow: …. m3/h

- External static pressure, supply airflow: …. Pa

- External static pressure, extraction airflow: …. Pa

- Cooling Coil Capacity: …. kW

Assembly Options

Unit to be available in following configurations to match application-specific requirements:

Component Description

Casing

Unit casing to be made of galvanized steel metal sheets pre-painted with white colour RAL 7035 polyester paint. Unit frame to be self-supporting (i.e. to be able to bear unit load with no plastic deformation).

Air Circuit

Reusable air filters to be pre-fitted in unit assembly. Coils to be made of copper pipes mechanically expanded into aluminium fins achieving high thermal efficiency. Coils to be fitted with condensate drain pans. Unit to be equipped with centrifugal fan(s) coupled by pulleys and belts. Fan(s) to be fitted on greased spherical bearing so that no maintenance is required. Fan(s) to be equipped with double-intake turbines and front-curved blade impeller(s). Fan(s) to be driven by electric motor(s) equipped with tensions. Motor(s) should have internal thermal protection and be Class F and IP55 protection certified. Option to replace belt-driven supply air centrifugal fan(s) with plug type EC fan(s) equipped with
built-in variable speed control.

Cooling Circuit

Circuit to be equipped with thermostatic expansion valve(s) with external equalisation.

Protections

Unit to be equipped with main door switch.

Optional Components

Corrosion Protection

The following options should be available to ensure coil protection under corrosive conditions:

- Coil made of copper pipes mechanically expanded into copper fins.

- INERA® coil made of copper pipes mechanically expanded into high-performance aluminium-alloy fins.

- Coil made of copper pipes mechanically expanded into aluminium fins with polyurethane and Blygold® coating.

- Stainless steel condensate drain pan.

Humidity Protection

The following options should be available:

- Indoor coil droplet eliminator option. Recommended for applications where a high air moisture content is expected.

- Fresh air intake droplet eliminator option.

Comfort/heating options

- Hot water auxiliary coil fitted with a three-way valve. Two options shall be available:

  - Primary Heating Coil in cooling-only units.

  - Auxiliary Heating Coil in reversible heat pump units.

Should the unit include a hot water coil and be equipped with free-cooling option, an anti-frost thermostat is to be installed if the unit operates at low ambient temperatures.

- Auxiliary Electrical Heaters: Air flow controller shall be included if an auxiliary electrical heater option is selected.

Indoor Air Quality

The following filter options shall be available:

- Supply air side filtration:

  - G4 class gravimetric filter.

  - G4 class gravimetric filter + creased opacimetric F6 to F9 class filters.

- Return air side filtration (should belt-driven centrifugal fan(s) be selected):

  - G4 class gravimetric filter.

  - G4 class gravimetric filter + creased opacimetric F6 class filter.

Safety

- Supply and return fan soft starter option. This option shall only be available for belt-driven centrifugal fans. Option shall be compulsory for motors with a rated output equal or more than 15 kW.

- Differential pressure switch for the detection of filter clogging.

- Differential pressure switch for air flow control.

- Smoke detection station in accordance with NF S 61-961 standard requirements.

- Refrigerant leak detector option. This allows for the prompt identification of gas leakages, hence ensuring occupant safety. Installation of the device ensures F-GAS, EN378 and ASHRAE 15 standards compliance.

Installation

- Anti-vibration rubber mounts.

- Configurable position of supply and/or return air side (several assemblies to choose from).

- Option to select supply and/or return fan(s) with high available static pressure.

- Option to replace belt-driven centrifugal fan(s) with plug type EC fan(s). Option to only be available for supply fan.

- Assemblies with mixing box for fresh air intake and free-cooling available. Two (2) or three (3) motorised damper options to be available.

Free-Cooling Option

Units equipped with mixing box shall be able to function on free-cooling mode regulated by central electronic control. This function shall allow the exploitation of outdoor air conditions to reduce load on coil. Dampers shall be available to regulate the percentage of outdoor air flow (0% to 100% variation). Economizer control should be thermo-enthalpic i.e. economizer should work by comparing requested and outdoor air enthalpy and temperature values. This is the optimum solution as it takes climate variability into account. Thermal and enthalpic economizer control shall also be available as alternative options.