Package Rooftop Supply:

Package Rooftop unit shall be factory assembled single piece for outside installation, Carrier model 48UAXXX type.

50UAXXX type.

48UHXXX type.

50UH XXX type.

The Package Rooftop unit shall use the R410A refrigerant with efficient thermodynamic characteristics, and shall be equipped with scroll compressors.

- The 48/50 UA/UH unit shall comply with the requirements of the following European regulations

    - Machinery 98/37/CE revised,

    - Low voltage directive 2006/95/CEE

    - Electromagnetic Compatibility directive 2004/108/CEE and the applicable recommendations of the European standards.

    - Machine safety: electrical equipment in machines, general regulations, EN 60204-1,

    - Electromagnetic Emissions radiated: IEC 61000-3-3

    - Electromagnetic Emissions canalised: IEC 61000-6-4

    - Electromagnetic immunity: IEC 61000-6-2

- General description

Unit(s) shall be designed, manufactured and tested in a facility with a quality assurance system certified ISO 9001 and with an environment management certified ISO 14001.

Unit(s) shall be certified by Eurovent.

Unit(s) shall be run tested at the factory before shipment.

- Design performance data

Cooling capacity:	kW

Compressor power input:	kW

EER : 	kW/kW

Energy class coefficient cooling (@Eurovent conditions) :

Heating capacity:	kW

Heating capacity (integrated with defrost cycles):	kW

Compressor power input:	kW

COP :	kW/kW

Energy class coefficient heating (@Eurovent conditions):

Outside Air Temperature: 	°C

Outdoor weighted Sound Power Level:	dB(A)

Indoor Supply duct weighted Sound Power Level:	dB(A)

As standard, the unit shall be able to start up and operate thermodynamic at full load with ambient temperatures ranging from -10°C to 48°C.

- Compressors

- Hermetic scroll type compressors featuring a limited number of moving components and are equipped with a two-pole electric motor cooled by suction gas.

- Further compressor protection is offered by an active protection against the presence of liquid at the inlet and an advanced protection against over-temperature at the outlet.

- Individual oil sight glass(es) shall be located on the equalization line allowing oil level measurement of oil level when unit(s) are non operational.

- The compressor shall be charged with synthetic polyester oil.

- Units are to be fitted with electric crankcase heaters to maintain optimum lubrication of the compressor scrolls at start up.

- Monitoring of the compressor operating map shall be ensured by the Pro-Dialog+ control (including overheat, low and high pressures).

- The compressor mountings shall be independent from the unit chassis and installed on flexible anti-vibration blocks.

- Suction and discharge piping support on the compressor discharge side, directly attached to the compressor base to prevent the transmission of vibrations to the unit chassis.

- Air Heat Exchanger

- All coils shall be made of high-quality staggered copper tubing, mechanically bonded in pre-coated corrugated aluminum slit fins mechanically expanded onto copper tubes, with high-level protection against corrosion and UV slit fins.

- Coils defrost shall be optimized by the auto-adaptive algorithm from ProDialog+ controller to reduce the defrost cycle duration.

- Unit(s) shall be fitted an electric heater preventing accumulation of ice on the air heat exchanger base.

- All pipes and refrigeration components shall be welded to eliminate leakage risks.

- Outdoor fans

  - Carrier Flying Bird low-noise direct-drive fans with 11 blades and rotating shroud made of a corrosion-resistant composite material. Three phase motor, dual speeds  insulation F class IP55 water protection and overload protection. Vertical discharge with Steel wire Protection grills coated with polyethylene.

- Indoor fans

  - Double-inlet indoor fans have forward-curved blades. They are statically and dynamically balanced for quiet, vibration free operation and factory-set to supply nominal air volume and static pressure. The fans are powered by generously sized three-phase motors via adjustable belt and pulley transmission.

- Indoor Air Quality & Filters sections

  - The Unit(s) shall use either standard G4 filters or an optional two-stage pre-filter and final filter G4 + F7 or F6 + F7 high-efficiency filters (all fire class M1) Filter classes are specified in accordance with EN 779-2002.

  - Unit(s) shall be factory fitted with 2 filters rack minimum 50mm to allow good filters serviceability.

  - Unit(s) shall be fitted with optional filter differential pressure switch to indicate if the filter is dirty.

- Refrigerant circuit

  - Each refrigerant circuit is fitted with: a liquid valve, sight glass a filter drier, an thermostatic expansion valve, pressure and temperature sensors, high pressure switch with manual reset from the interface on the high pressure side and R410A refrigerant charge.

  - All the refrigerant circuit components are brazed for total and lasting leak-tightness.

  - Leak-tight refrigerant circuit using the latest refrigerant circuit technology from Carrier Aquasnap® chillers ranges including:

    - brazed refrigerant connections for increased leak tightness,

    - elimination of capillary tubes,

    - secured access to pressure transducers and temperature sensors without losing refrigerant charge.

- Electrical box for power and control

  - The electrical box is composed with separated compartments with doors on hinges: one compartment is for control and the other for the power. The power section is closed with a disconnect/isolating switch.

  - A single 3 phase power supply without neutral for the unit.

  - The control circuit voltage shall be 24 V by a factory-installed transformer.

- Chassis/enclosure

- Chassis and enclosure made of galvanized sheet steel. Painted in oven-baked polyester powder paint in light grey colour (RAL 7035).  The removable panels and the doors shall be accessible by 1/4-turn screws.

Unit control Pro-Dialog+

- Sophisticated Pro-Dialog+ control combines intelligence and ease of use and permanently supervises all operating parameters to optimise and closely manage operation of compressors, expansion valves and fans to minimise energy consumption and maximise unit efficiency at all operating conditions.

Pro-Dialog+ features the following functions:

- Control

  - PID loop with equalization of the compressor operating times and number of compressor start-ups. The system shall adapt to the installation inertia and prevent the excessive compressor cycling.

  - Control of the condensing pressure by an auto-adaptive algorithm (fan speed).

  - Set point offset in function of the ambient air temperature

  - Balance of number of start and operating time of the compressors and fans (except size 45).

  - Set points shall be available for summer and winter operation, occupied and unoccupied periods (over 8 periods maximum a day).

- Safeties

  - The system shall monitor the evolution of operating parameters (including temperatures, etc.) and shall adjust to maintain the compressors in its operating range. Should a parameter exceed its maximum value, an alarm message shall be generated and only if necessary the unit shall stopped.

  - Conditions that shall stop the refrigerant circuit or the unit include:

    - Low Suction pressure

    - High discharge pressure.

    - Permanent low or high superheat.

    - Electrical overload on compressors.

    - Default on the temperature sensor or on the pressure transducer.

    - Card default or communication loss.

    - Customer specific safeties.

  - More the 50 alarm codes of default permit to determine the origin of the incidents.

- User interface

- The new back lit LCD display equipped with a manually operated potentiometer to allow the operator to adjust the luminosity according to ambient light conditions.

- The data are displayed in full text in French, English, German, Italian, Spanish (other language please consult your Carrier salesman).

- Navigation with the Pro-Dialog+ is via an intuitive tree structured menu very similar to web navigators.

- Whilst easy to use, menus still allow quick access to all main operating parameters including: Number of compressors on, suction/relief pressure, compressor operating time, set-points, Air temperature, entering/leaving water temperature.

- Remote unit control

  - A single 2 wire communication bus between the Pro-Dialog+ RS485 serial port and the Carrier Comfort Network offers control, monitoring and diagnostic solutions.

- Dry contact entries allow:

  - Start/stop: The contact opening makes the unit stops.

  - Dual set point: the contact closing activates a second set-point (example: unoccupied mode).

  - Capacity limitation 1 and 2: The closing of the contact limits the maximum capacity at 3 predefined values.

  - User safety: this contact may be used for any customer safety loop, the closing contact generates a specific alarm.

  - Connection to Carrier thermostat 33CS.

- Discreet Outputs are available for:

  - Alarm signal: This dry contact shall indicate a major default resulting in the stop of one or both refrigerant circuit(s).

  - Compressor operation: this contact may be used to provide indication of compressor operation.

- Internal clock allowing programing of following operating modes:

  - 7 days scheduling: Start and stop unit / liquid temperature re-set.

  - Setpoint reset based on ambient temperature.

  - Master/Slave operation of both units in parallel with operating time balancing between units and change over in case of failure.

  - Change-over based upon ambient air temperature.

- Night mode:

  - Capacity and fan speed limitation to reduce night time sound levels.

- Defrost function:

  - The defrost cycle is applied to one circuit at a time.

  - The defrost cycle is fully automatic and does not require any setting. A condensate heater prevents ice formation at the bottom of the heat exchangers, if the defrost cycles are taking place at low outdoor temperature.

  - The indoor fans run during the defrost cycle except in single-circuit units without additional heat option (electric heat stage or hot-water coil).

- Purge function:

  - When the unit switches from unoccupied to occupied mode, the economizer is kept fully open for two minutes provided the outdoor temperature is between 10°C and 21°C, allowing CO2 and odours clean up.

- Smart Start:

  - This mode permits heating or cooling the room before it is occupied so that the space temperature has reached its setpoint at the beginning of the occupied period.

- Test Menu Service:

  - ProDialog+ controller gives end-user or the service technicians to check below listed parts of the unit before start-up and ensure quick commissioning and diagnostics :

    - Compressor(s)

    - Indoor fan

    - Outdoor fan(s)

    - Electrical heater

    - 4 way valve (UH)

    - Defrost heater

    - Power exhaust (opt)

    - Alarm output test

    - Economiser analog control (opt)

    - Hot water coil 3 way valve (opt)

Options:

- Pre-treated coils (outdoor & indoor) fins

Precoated  aluminum fins (polyurethane). Better resistance to corrosion, recommended for marine ambience.

- Economizer

  - An optional integrated economizer permits cooling utilising an outdoor air sensor.

  - Economiser is offering two possible control type: dry-bulb temperature differential or enthalpy differential.

  - For outdoor enthalpy control the economizer is provided with two enthalpy sensors for optimum temperature and humidity control.

  - The direct gear-driven, low-leakage blades eliminate conventional inter-blade linkages and associated adjustments.

  - The economizer operates in conjunction with mechanical cooling, when required, and is factory-installed for either vertical or horizontal operation. The factory-supplied and field-installed rain hood/filter assembly is designed to revent moisture or objects from entering the unit.

  - The Economizer is controlled by Carrier Pro-Dialog+ controller, to support the requirements of indoor air quality control, using outside air. Units can either be equipped with an adjustable, self-closing outside air economizer or a fully modulating economizer. The economizer can be configured for a full modulation mode or three-position operating mode.

  - The control includes a logic for a minimum ventilation position and different set points for occupied and unoccupied minimum position set points.

- Indoor fans - Variable Air Volume

  - The belt driven high static centrifugal fan is driven by a Variable Frequency Drive on motor.

  - Operating mode can be selected by the user from control panel’s user interface either constant air volume mode or variable air volume mode.

  - In constant air volume mode supply fan speed is adapted to maintain airflow rates according to air duct pressure drop.

  - In variable air volume mode the unit automatically determines the minimum airflow need to provide a satisfying room air temperature and maximize energy efficiency.

- Energy Recovery Module (ERM)

  - The ERM is an individual dual-flow unit, equipped with a high-efficiency Eurovent-certified air-to-air heat recovery wheel with 63% to 88% efficiency, an integrated variable air-volume plug fan and a control system for plug-and-play installation.

  - The unit cabinet is made of galvanised and powder-painted sheet metal, especially suitable for outdoor use, for double corrosion protection (light-grey colour RAL 7035).

  - The ERM is fitted with G4 filters on the fresh-air side as standard to protect the heat recovery wheel against dust.

  - High-efficiency plug fans for exhaust air. The direct-drive fans do not suffer any belt and pulley drive losses. They are more energy-efficient and require less maintenance.

  - The exhaust air fan speed is independently controlled by frequency inverters directly connected to the Pro-Dialog+ controller inside the rooftop unit.

  - When outside conditions permit, the control system continuously adjusts the fan speed to minimise power consumption.

  - The ERM option is delivered as a single piece for fast installation, separate from the rooftop units. An insulated sheet metal kit and a wiring kit are provided by the factory for easy connection between rooftop and ERM unit.

  - To facilitate installation, the ERM is factory-fitted with a terminal block for the power and control wiring for easy connection to the rooftop units, wiring is factory supplied to match factory air duct kit installation only. The control box and the sensors are factory installed and tested for fast and trouble-free start-up.

- Indoor fan Soft starter

Indoor fan motor shall start progressively to reduce noise and start-up current.

- Gas heating solutions (48UA/UH only)

  - Tubular, dimpled gas heat exchanger design permits hot gases to make multiple passes across the path of the supply air.

  - The dimpled design creates a turbulent gas flow to maximise heating efficiency.

  - The extra-thick Alumagard™ heat exchanger coating provides corrosion resistance and ensures long heat exchanger life.

  - Modular heater compartment assembly consists of a series of injectors. The gas-air mixture, prepared in the heaters, enables excellent combustion within the heat exchanger tubes. The direct spark ignition system saves operating expense.

  - Induced draft combustion system eliminates the unsightly appearance of flue stacks and minimises the effects of wind on heating operations. The inducer fan draws hot combustion gas through the heat exchanger at the optimum rate for the most effective heat transfer. For improved efficiency the heat exchanger operates under negative pressure, preventing flue gas leakage into the indoor supply air.

  - The gas heating system uses multiple heating sections. Each section is equipped with a two-stage gas valve. The gas valves are sequenced by a factory-installed integrated gas controller (IGC) with CE mark.

  - The heating safety controls shall shut down the unit if they detect a problem, six safety levels are operating:

    - Temperature limit switch for indoor fan shutdown failure.

    - High-temperature limit switch for reduced air flow.

    - Air pressure switch to ensure sufficient combustion gas flow.

    - Rollout switch to avoid flame rollout.

    - Flame detection by ionisation to quickly sense the heater flame.

    - Gas pressure switch to avoid operation at low supply pressure (<10 mbar).

- Hot-water coil with three-way valve (50UA/UH only)

  - The hot-water coils offer a fully modulating proportional three-way valve as standard, with supply air temperature based control.

  - Option includes two isolating shut-off valves factory-fitted, wired and fully factory-tested.

  - Frost protection is provided by a low-temperature sensor and the coils are equipped with a purge system.

- Electric heater (50UA/UH only)

  - Shielded electric resistance heaters are fully factory-wired and tested.

  - Each stage is protected against overloads by two thermal protectors.

  - The low-limit protector with automatic reset is located above the resistance heaters while the high-limit protector with manual reset is located in the heater control box.

  - This high-temperature limit control offers overload protection.

- Indoor air quality CO2 sensor

  - Allow good Indoor Air Quality by controlling CO2 concentration levels in the building.

- Stainless steel pan

  - Easy-to-clean drain pan for improved hygiene and easy condensate draining.

- Dirty-filter detection

  - Alarm reported by adjustable differential pressure switch connected to ProDialog+ controller.

- Supply air flow detection

  - Alarm reported by adjustable differential pressure switch connected to ProDialog+ controller.

- Smoke detection

  - Building fire safety based on smoke detection.

- Fire thermostat

  - Generates general unit fault if thermostats detect return air temperature above adjustable temperature (factory-set to 70°C). Manually reset thermostat in return air duct.

- Fixing frame

  - Rigid metallic frame on air return and supply sides for easy air duct installation.

- J-Bus Gateway

2 way communication card with J-Bus protocol.

- Lon Talk Gateway

2 way communication card with Lon Talk protocol

- BacNet Gateway

2 way communication card with BacNet protocol

Accessories:

- Remote ProDialog+ interface

User interface that can be mounted up to 300 metres from unit (bus communication) allowing same level of access to control menus as unit mounted interface for mounted inside building.

External Electrical  220V/24V transformer shall be supplied to  be installed on-site.

- Vertical supply roofcurb

Galvanised steel 2 mm thick frame for vertical supply and vertical return air.

- Vertical adjustable longitudinal supply roofcurb

Galvanised steel 2 mm thick frame for vertical supply and vertical return air with on site adjustable longitudinal slope up to 5%.

- Vertical adjustable transversal supply roofcurb

Galvanised steel 2 mm thick frame for vertical supply and vertical return air with on site adjustable transversal slope up to 5%.

- Horizontal supply roofcurb

Galvanised steel 2 mm thick frame for horizontal supply and horizontal return air.