General Description

Precision air-conditioning cabinet with compact footprint and dual-wall construction designed specifically for the air handling requirements (e.g. filtration, temperature and humidity control) of computer, telecommunications and specific purpose rooms (such as sensitive storage, controlled atmosphere rooms, etc.). Unit to be equipped with EC motors (electronically commutated motors with built-in variable speed control) and PLC control thanks to which unit energy consumption is reduced. Unit to be able to be equipped with hydraulic and direct expansion (DX) coils according to customer preference and/or application-specific requirements. Unit to be available in various configurations 
(minimum number of configurations deemed acceptable depicted in figure below) to meet site-specific installation requirements.

Products across entire range to be ISO 9001 and ISO 14001 certified.

Unit Specification

Unit technical characteristics:

- Volumetric Airflow Rate: …. m3/h

- External Static Pressure: …. Pa

- Cooling Coil Capacity: …. kW

- Heating Coil Capacity (if applicable): …. kW

- Electric Heater Capacity (if applicable): …. kW

Component Description

Casing

- Robust dual-wall construction.

- Close Control Unit (CCU) to be made of self-supporting, double-skin panels of steel metal sheets, galvanised on both sides to ensure a stiff and corrosion-resistant exterior envelope.

- Minimum internal metal sheet thickness: 0.8 mm.

- Minimum external metal sheet thickness: 1 mm.

- External CCU envelope sheet to be pre-coated in grey RAL 7035 to enhance durability in corrosive conditions.

- Unit to be insulated with no less than 25 mm thick glass wool insulation. Envelope insulation ensures the absence of thermal bridges between the internal and external surfaces of the CCU, minimizing the potential for condensation and unwanted heat transfer.

- Minimum acceptable Euro Class Fire Rating: A1.

Filtration

- F2SI type filter cells, minimum acceptable rated efficiency: 90% (ASHRAE gravimetric test G4).

- Option to add F7 opacimetric filtration cell.

- Option to add two-stage filters (e.g. G4 + F7).

- Filter to be airtightly connected to CCU frame by means of a specially designed gasket to ensure minimal filter bypass leakage.

- Filter fouling level to be monitored using analogue pressure sensor.

Cooling Coil

- Coils to be made of copper tubes mechanically expanded into aluminium fins achieving high thermal efficiency.

- Condensate drain pan to be pre-fitted under all cooling coils.

- Units with hydraulic cooling coils to have 2- or 4- way control valve pre-fitted and connected. Option to include thermally insulated flexible connections.

- Units with DX coils to have thermostatic expansion valve pre-fitted.

Fans

- Direct-drive centrifugal fans to be driven by EC motor 1-Ph/230V/50-60Hz, 4-pole, Class F.

- Fan speed to be variated via either manual user adjustment or automatic controller adjustment based on room load and system air control indications.

- Airflow rate to be monitored by analogue pressure sensor.

Electrics Box

Electrics box minimum features:

- Power supply: 3-Ph/400V/50Hz + T + N.

- Pre-fitted emergency stop disconnect switch.

- 3-Ph 400/24V transformer with protection.

- Fan motor protection and control.

- Depending on options selected: Capacity to protect and control humidifier and electric heater.

- Regulated by CCU Controller.

- Return air dry-bulb temperature control.

- Return air humidity control.

- Option: supply air humidity control.

- Option: dehumidification control.

- Option: water leak detection, fire thermostat and supply air low-limit monitoring.

- Option: condensate drain pump.

- Remote control and fault summary contact.

Optional Components

Electric Heater

- Fan-controlled operation.

- Two-stage control (except for 3 kW electric heater).

- Two-stage or TRIAC control.

- Two (2) high-limit safety thermostats; one (1) automatic and one (1) with manual reset.

Hot Water Coil

- 1-row hydraulic coils to be made of copper tubes mechanically expanded into aluminium fins achieving high thermal efficiency.

- Pre-fitted and connected 2- or 4-way control valve.

- Option to include thermally insulated flexible connections.

Humidifier

- Immersed electrode humidifier with large surface area stainless steel electrodes. Humidifier to be designed to operate on municipal water supply only (water conductivity 350 to 1250 μS and hardness 15 to 30°F).

- Humidifier information to be available directly on CCU Controller.

- Electronics board to be available for operation management.

- Steam cylinder to be designed to ensure easy component removal.

- Filling solenoid valves to be included.

- Drain pump to be included.

- Water supply connection kit to be included.

- Performance:

  - Minimum of 3 kg of steam per hour for nominal airflow rate < 3,000 m3/h.

  - Minimum of 8 kg of steam per hour for nominal airflow rate > 3,000 m3/h.

Control

- Configurable controller to be equipped with 160-character display. Capacity to display unit operating instructions, operating states, fault codes and solutions.

- Fault codes to be arranged in two fault levels.

- Capacity to monitor unit operating times.

- RS 485 output with Jbus/ModBus protocol.

- Capacity to manage unit rotations, backups and top-ups.

- Option: LON gateway.

- Optional changeover thermostat (only available on units with hydraulic coils).

Component Description (DX coil units only)

Scroll Compressor

- Air-cooled condenser to be made of copper tubes mechanically expanded into aluminium fins.

- All-season operation. Ambient temperature operating limits: -15°C to +45°C.

- Crankcase resistance option to be available.

- Either one (1) or two (2) variable speed EC motor propeller fan(s) depending on selected model.

- Condensation pressure control to be achieved by fan speed variation. Fan speed to be driven by pressure sensor readings.

- Refrigerant connections (FLARE connections).

- Robust yet light-weight casing to be made of recyclable synthetic and UV stabilised material.