General Description

Precision air-conditioning cabinet with compact footprint and dual-wall construction to be designed specifically for the air handling requirements (e.g. filtration, temperature and humidity control) of computer, telecommunications and specific purpose rooms (such as sensitive storage, controlled atmosphere rooms, etc.). Unit to be equipped with EC motors (electronically commutated motors with built-in variable speed control) and PLC control thanks to which unit energy consumption is reduced. Unit to be available in various configurations (minimum number of configurations deemed acceptable depicted in figure below) to meet site-specific installation requirements.

Product across entire range to be ISO 9001 and ISO 14001 certified.

Unit Specification

Unit technical characteristics:

- Volumetric Airflow Rate: …. m3/h

- External Static Pressure: …. Pa

- Cooling Coil Capacity: …. kW

- Heating Coil Capacity (if applicable): …. kW

- Electric Heater Capacity (if applicable): …. kW

Component Description

Casing

- Robust dual-wall construction.

- Close Control Unit (CCU) to be made of self-supporting, double-skin panels of steel metal sheets, galvanised on both sides to ensure a stiff and corrosion-resistant exterior envelope.

- Minimum internal metal sheet thickness: 0.8 mm.

- Minimum external metal sheet thickness: 0.8 mm.

- External CCU envelope sheet to be pre-coated in grey RAL 7024 and 7035 to enhance durability in corrosive conditions.

- Unit to be insulated with no less than 25 mm thick glass wool insulation. Envelope insulation ensures the absence of thermal bridges between the internal and external surfaces of the CCU, minimizing the potential for condensation and unwanted heat transfer.

- Minimum acceptable Euro Class Fire Rating: A1.

Filtration

- Available filters: G4 and F7.

- Option to add two-stage filters (e.g. G4 + F7).

- Filter to be airtightly connected to CCU frame by means of a specially designed gasket to ensure minimal filter bypass leakage.

- Filter fouling level to be monitored using analogue pressure sensor.

Hydraulic Cooling Coil

- Coils to be made of copper tubes mechanically expanded into aluminium fins achieving high thermal efficiency.

- Condensate drain pan to be pre-fitted under all cooling coils. Condensate drain pans to be made of either stainless steel or aluminium.

- Cooling coils to have 2- or 3- way control valve pre-fitted and connected.

Fans

- Direct-drive centrifugal fan driven by EC motor 1-Ph/230V/50-60Hz, 4-pole, Class F.

- Fan speed to be variated via either manual user adjustment or automatic controller adjustment based on room load and system air control indications.

- Airflow rate to be monitored by analogue pressure sensor.

- Fan to be equipped with ModBus card to allow for the transmission of faults and settings (such as actual power input, current, rotation speed, etc.).

Electrics Box

Electrics box minimum features:

- Power supply: 3-Ph/400V/50Hz + T + N.

- Main disconnect switch.

- 3-Ph 400/24V transformer with protection.

- Protection and control of all electrical components by means of contact breakers and switches.

- Regulated by CCU Controller:

  - Return air dry-bulb temperature control.

  - Return air humidity control, in supply or dehumidification mode.

  - Water leak detection.

  - Remote control and fault summary contact.

Optional Components

Electric Heater

- Fan-controlled operation.

- Two-stage or progressive action (TRIAC) control.

- Two (2) high-limit safety thermostats; one (1) automatic and one (1) with manual reset.

Hot Water Coil

- 1-row hydraulic coils to be made of copper tubes mechanically expanded into aluminium fins.

- Pre-fitted and connected 2- or 4-way control valve.

Humidifier

- Immersed electrode humidifier with large surface area stainless steel electrodes. Humidifier to be designed to operate on municipal water supply only (water conductivity 350 to 1,250 μS and hardness 15 to 30°F).

- Humidifier information to be available directly on CCU Controller.

- Electronics board to be available for operation management.

- Steam cylinder to be designed to ensure easy component removal.

- Filling solenoid valves to be included.

- Drain pump to be included.

- Water supply connection kit to be included.

- Minimum steam flow rate: 8 kg/h.

Control

- Configurable controller to be equipped with 160-character display. Capacity to display unit operating instructions, operating states, fault codes and solutions.

- Fault codes to be arranged in two fault levels.

- Capacity to monitor unit operating times.

- RS 485 output with Jbus/ModBus protocol.

- Master/slave management type capacity.

- Option: LON gateway.

- Option: Pressure variation in raised floor configuration.

- Optional changeover thermostat.