General Description

Packaged rooftop unit consisting of autonomous, compact air to air units for the treatment of indoor air. Rooftop unit to be available in two (2) configurations to allow both cooling-only and reversible heat pump operation. Unit should also be available in two (2) arrangements: “standard” and “in-line” depending on supply air flow direction. Unit should be designed for optimum part-load performance achieving the highest levels of seasonal efficiency and exceeding the minimum requirements set by EU Regulation 2016/2281 (Lot 21). Unit should feature mono-block lightweight construction designed specifically to ensure easy installation and unit maintenance. Unit should be field-convertible to meet site-specific installation requirements (i.e. be able to be converted from a vertical air flow to a horizontal air flow arrangement). Product should be equipped with the latest HVAC technological innovations featuring multi-scroll compressors, electronic expansion valves, electronically commutated (EC) motors with built-in variable speed control as well as auto-adaptive microprocessor control system. For maximum adaptability, several options should be available including exhaust air energy recovery sections, economizers, indoor air quality management systems and auxiliary heating modules.

| Ecodesign Requirements for Rooftops & Package Units (EU Regulation 2016/2281) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cooling | January 2018 |  | January 2021 |  |
|  | ηs,c % Primary Energy | SEER | ηs,c % Primary Energy | SEER |
| Cooling-only air to air rooftop units | 117 | 3.00 | 138 | 3.53 |
| Heating | ηs,h % Primary Energy | SCOP | ηs,h % Primary Energy | SCOP |
| Heat pump air to air rooftop units | 115 | 2.95 | 125 | 3.20 |

Unit Operating Limits

Unit should meet the following minimum operating limit requirements:

| Inlet Air Conditions |  | Cooling | Heating |
| --- | --- | --- | --- |
| Indoor Coil | Minimum Temperature | 9.67 oC WB | 10 oC DB |
|  | Maximum Temperature | 24 oC WB | 27 oC DB |
| Outdoor Coil | Minimum Temperature | 12 oC DB | -15 oC WB |
|  | Maximum Temperature | 48 oC DB | 15 oC WB |

Directive Compliance

Product to be ISO 9001 and Eurovent certified. Product should comply with the following directives and standards:

- Machinery Directive 2006/42/EC (MD).

- Electromagnetic Compatibility Directive 2014/30/EU (EMC).

- Low Voltage Directive 2014/35/EU (LVD).

- Pressure Equipment Directive 2014/68/EU (Category 2) (PED).

- RoHS Directive 2011/65/EU (RoHS).

- Ecodesign Directive 2009/125/EC.

- Energy Labelling Directive 2017/1369/EU (Eco-Labelling).

- Harmonised Standard: EN 378-2:2012 (Heat Pumps - Safety and Environmental Requirements).

Assembly Options

Unit to be available in following configurations to match application-specific requirements:

Unit Specification

Unit technical characteristics:

- Supply airflow: …. m3/h

- Extraction airflow: …. m3/h

- External static pressure, supply airflow: …. Pa

- External static pressure, extraction airflow: …. Pa

- Cooling Coil Capacity: …. kW

- Maximum coil velocity: …. m/s

Component Description

Casing

Unit to have double wall panels. Casing to be made of galvanised steel metal sheets pre-coated with white-colour
(RAL 7035) polyester paint. Rooftop frame should be self-supporting (i.e. able to bear unit weight with no plastic deformation). For ease of transportation, units should be able to be stacked in groups of two (2) without the need to be supported by a wooden pallet. Panels should be removable to ensure ease of access to all unit components. 
Unit should be thermally and acoustically insulated with ceramic fibre insulation and a minimum Euroclass fire classification of A2-s1, d0(M0).

Internal Unit Section

Supply air flow side to be equipped with:

- Condensate drain pan for corrosion-protection.

- Option to include room overpressure management. In installations with different supply and return air flows the fresh and exhaust air damper will be managed independently to prevent the entry of outdoor air and/or eliminate indoor odours.

- Filter fouling to be monitored with differential pressure switches.

Outdoor Unit Section

Unit to be equipped with:

- Outdoor coil protection grid.

- Droplet eliminator at fresh air intake.

- Unit to be mounted on anti-vibration rubber mounts.

Filters

The following filter options should be available:

- Low pressure drop G4 filters.

- Folded filters: G4 + M6, F7 and F9.

- Low pressure drop folded filters: G4 + F7 and F9.

- Double stage folded filters: M6 + F7, M6 + F9, F7 + F9 and F9 + F9.

Cooling Circuit

Cooling circuit to feature R-410A hermetic scroll-type compressors connected in tandem to achieve excellent
part-load efficiencies. Compressors to be mounted on anti-vibration pads. Electronic expansion valves to be used for performance and safety. An electric crankcase heater shall also be fitted on each compressor. Each cooling circuit to be equipped with an oil sight glass, filter drier, pressure and temperature sensors and high-pressure switch. Four-way cycle reversing valve to be fitted on reversible heat pump units.

Heating Elements

Unit should be able to incorporate one of the following heating elements:

- Auxiliary electrical heaters, with two power stages and on/off control, for assembly and connection inside the unit. A minimum of two (2) total power options should be available for each model.

- Auxiliary hot water coil, with three-way valve and proportional control, for assembly inside the unit.

  - The unit should incorporate a freeze protection thermostat.

  - Hot water coil to be available in two (2) variants:

  - Standard variant where the only safety system is the freeze protection thermostat.

  - Very low outdoor temperature variant with freeze protection technology based on water temperature. This option should incorporate a circulation pump as well as two sensors inserted in coil input and output. For outdoor temperatures lower than -20ºC WB this variant should be selected as standard.

- Gas-fired condensing boiler with hot water coil. Natural or propane gas boiler with modulating actuator, in accordance with Gas Directive 2009/142/EC mounted on unit side.

  - Electronic ignition burner to be equipped with premixing and modulation technology that allows for outputs close to 109%.

  - Heat exchanger to be made of stainless steel with low carbon content.

  - Proportional air/gas valve to be available.

  - Class 5 NOx emissions (EN 297).

  - Condensate drain pan fitted with siphon to be available.

  - Safety devices: safety thermostat, low water pressure safety switch, flowmeter, Delta-T control, smoke temperature sensor.

  - Negative Temperature Coefficient (NTC) sensor fitted for boiler water temperature regulation.

  - Water working temperature: -7ºC to 100ºC.

  - Electronic controller with microprocessor and Multifunction LCD display for boiler control, configuration and diagnostics. Capacity to incorporate ModBus communication.

  - Boiler connected to auxiliary coil water circuit.

  - Type of gas used to be optimised for country-specific applications.

  - Water circuit (installed inside the unit) to include:

    - Water coil.

    - Circulation pump.

    - Expansion vessel.

    - Gate valves.

    - Safety valve.

    - Automatic air bleeder valve.

- Warm air heater module with gas burner and modulating actuator, in accordance with Gas Directive 
2009/142/EC, installed inside a pre-assembled roofcurb.

  - Condensation boiler with premixing and modulation technology that allows for outputs close to 109% with respect to lower heating value (LCV). A minimum of two (2) total power options should be available for each model.

  - Class 5 NOx emissions (EN 297).

  - The combustion chamber and burner to be made entirely of stainless steel.

  - Electronic controller with microprocessor and multifunction LCD display, located inside the burner, for burner control, configuration and diagnostics.

Additional Heating Module

Module equipped with heat recovery coil. Coil function is to pre-heat air that passes through the main indoor coil. For this purpose, it uses the temperature of an outdoor water installation.

Coils

Coils to be available in following options/variants:

- Coils made of copper pipes and fins.

- Coils made of copper pipes equipped with polyurethane pre-coated aluminium fins.

- INERA® coils made of copper pipes equipped with aluminium fins designed for excellent thermal performance and great corrosion-resistance.

- Blygold® coated coils.

Heat Recovery

Active Recovery System

The unit is to be fitted with a thermodynamic circuit dedicated to the recovery of extracted energy. Recovery system is to be equipped with independent and proportional control adapted to air renewal requirements with the purpose of raising the seasonal energy efficiency of the rooftop unit. Units with fitted active recovery systems should feature:

- EC plug-fan in return air flow side.

- Air circuit equipped with coils made of copper pipes and aluminium fins.

- Electronic expansion valve.

- Hermetic scroll-type compressor with sound insulation assembled over antivibration mounts.

- Crankcase heater.

- Four-way cycle reversing valve.

- Anti-acid dehydrator filter.

- High- and low-pressure transducers.

- Condensate drain pan.

Indicative schematic diagram outlining the recovery process is given below:

Passive Recovery System

A heat recovery wheel is used to transfer sensible and latent heat from the return to the fresh air flow. Rotary heat wheel to be made of either aluminium for sensible heat recovery, epoxy-coated aluminium for sensible heat recovery in corrosive environments or silica gel coated aluminium for enthalpic recovery (high efficiency latent heat recovery). Hybrid wheel option should also be available for applications where enthalpic energy recovery is required. Wheel should be formed of two aluminium panels, one smooth and one fluted. The fluted panel should be provided in two (2) different configurations:

- 2.0 mm cross-section: commonly used cross-section due to its high efficiency and moderate pressure drop.

- 2.5 mm cross-section: designed for high frontal speeds with low pressure drop.

The wheel should be able to be equipped with a speed drive option which inhibits ice formation on the wheel during the winter. The speed drive should be fitted on all units that are expected to handle air streams with air temperature lower than 1 °C or rotary wheels that are expected to have a mean surface temperature of less than 3 °C.

Economizer

Units should be able to be equipped with economizer to allow for exploitation of favourable outdoor air conditions. With proper use of the economizer, coil capacity may be reduced. Dampers should be available to regulate the percentage of outdoor air flow (0% to 100% variation). Economizer control should be thermo-enthalpic i.e. economizer should work by comparing requested and outdoor air enthalpy and temperature values. This is the optimum solution as it takes climate variability into account. Thermal and enthalpic economizer control should also be available as alternative options. Units that are equipped with thermoenthalpic or enthalpic economizer control should be equipped with an outdoor air humidity sensor. The sensor is to either be supplied pre-fitted on rooftop unit or installed on another unit of the local network (pLAN).

Supply Fan

Direct-drive plug fans driven by EC motors with built-in variable speed control. Fan selection should be optimised based on designer-specified fan operating conditions. Range of fans to satisfy all pressure settings should be available.

Condenser Fan

Outdoor fan options:

- Two-speed direct-driven axial fan(s). Watertight motor class F, IP54 and internal thermal protection.

- Electronic axial fan(s) driven by EC motor.

All fans should have their propellers dynamically balanced. Protective grilles should be fitted on all fan propellers to avoid human injury and component damage.

Return Fan

Return fan options:

- Centrifugal return fan equipped with pulleys and belts. Electric motor equipped with tensioner, class F, IP55 and internal thermal protection. Fan to be equipped with front-curved blade impeller turbine. Fan to be mounted on greased spherical bearings.

- Direct-drive plug fan driven by EC motor with built-in variable speed control.

Electrical cabinet

Complete and fully pre-wired electrical cabinet to be available on all units. Electrical cabinet minimum features listed below:

- Electrical cabinet to be equipped with insulated access door to prevent condensation.

- Capacity to force-ventilate electrical cabinet.

- IP54 Protection.

- Wire numeration and identification of components. This is to simplify connection tracing and diagnostic tests.

- Hinges and quarter-turn latches on removable access door.

- Electrical power supply (with neutral).

- Main ground connection.

- Compressor and fan motor contacts.

Protection Systems

The following protection systems/mechanisms should be available:

- High pressure switches.

- High- and low-pressure transducers.

- Compressor discharge temperature control.

- Main door switch.

- Magneto-thermic protection switches for the power line of compressors and fan motors.

- Automatic switch in the control circuit.

Pre-assembled roofcurb

“Standard” unit arrangements to be equipped with pre-assembled roofcurbs of adjustable height, built of galvanised steel panels with polyester paint and thermal insulation. The levelling system should be fitted with angle pieces that allow adjustments to be made along the X- and Y- axes. “In-line” unit arrangements to be equipped with a wide range of adaptation roofcurbs.

Options

Low Ambient Temperature Protection

A range of frost protection options should be available for units operating in low ambient temperature environments.

- Frost protection option for outdoor ambient temperatures lower than -10 ºC WB.

  - Electrical heater for electrical cabinet component protection.

  - Low temperature protection equipped compressor.

  - Spring shut-off equipped dampers in case of power failure.

- Frost protection option for outdoor ambient temperatures lower than -14 ºC WB. Option features to include:

  - Reinforced electrical heater for electrical cabinet component protection.

  - Electrical heater for the anti-frost protection of economizer dampers (if applicable).

  - Gas burner low temperature protective kit (if applicable).

  - Spring shut-off equipped dampers in case of power failure.

Customised Functions

- Air Flow Zoning: up to four (4) different zones with a minimum air flow rate equal to 35% of the total supply flow. This function allows for the adaptation of indoor air flow rate to installation-specific requirements.

- Low Return Air Temperature: this function allows low temperature unit operation. Useful in food storage and pharmaceutical industry applications.

Sensors

Unit to be able to be equipped with the following sensors:

- Ambient temperature sensor(s).

- Dual ambient temperature-humidity sensor(s). Up to four sensors with RS485 communication or installed on the pLAN network. This sensor is compulsory in units with enthalpic or thermoenthalpic free-cooling.

- CO2 sensor for air quality control.

- Smoke detection control unit (to comply with NF S 61-961 standard requirements).

Miscellaneous Options Item 1

- Humidifier control (either on-off or proportional control).

- Electrical energy meter for power consumption monitoring.

- Cooling capacity meter. In addition to the energy meter, the unit incorporates mixing- and supply- air enthalpic sensors with RS485 communication that enable the determination of cooling and heating capacities.

Miscellaneous Options Item 2

- Compressor soft starter.

- High performance phase sequence relay used to adjust electrical power supply. Highly recommended for installations with power system voltage instability, lag between current and voltage, high level of electromagnetic disturbances EMC, etc.

- High grade switching devices.

- Varnish protection for electrical cabinet components: control board, cards and terminals.

Control

Factory-installed control to provide the capability for free standing operation or to be linked with a more extensive system. Factory-installed and programmed Modbus communication capability to provide simple integration with the building BMS system. Unit controller should also be configurable to communicate via LonWorks®, BACnetTM and Konnex protocols, if required by application. Unit control should have the capability to communicate with supervision solutions: pCO Web, PlantWatchPRO3 and BOSS. This communication flexibility is to allow simple system integration as well as data collection, monitoring and display of alarms. The control is to provide unparalleled service diagnostic information. The control should also be able to manage a local connection between units through a pLAN network (Local Area Network), allowing data and information to be exchanged between units (at least fifteen (15) units).

Functions of the control should include:

- Selection of setpoint and operating mode: Heating/Cooling/Auto/Ventilation.

- Continuous control of system operating parameters.

- Display of sensor values.

- Compressor cycles monitoring.

- Management of defrost operation.

- Supply air temperature control.

- All-seasons operation via condensation and evaporation pressure control.

- Setpoint compensation based on ambient temperature.

- Hourly and weekly schedule options.

- Fire protection.

- Error diagnosis.

- Management of all available components: economizer, back-up heating, CO2 air quality sensor,
heat recovery, etc.

User Interfaces

Graphic Terminal

Terminal to be fitted as standard on the electrical cabinet. It should be capable to provide control setting explanations in easy to understand English. No decoding required.

Terminal should be able to:

- Carry out unit initial programming.

- Modify operating parameters.

- Switch the unit ON/OFF.

- Select operating mode and adjust setpoints.

- Display the variables controlled and sensor values measured.

- Display the current and past alarms.

User Terminal (optional)

Terminal to be installed on the electrical cabinet (instead of the graphic terminal). In this case, remote connection of the graphic terminal should be possible.

User terminal should be able to:

- Switch the unit ON/OFF.

- Select operating mode and adjust setpoints.

- Display: indoor air temperature and humidity, outdoor air temperature, supply air temperature, CO2 sensor readings and damper control.

- Display alarm codes.

Touch Panel (optional)

Touch panel should be able to perform the same functions as the graphic terminal. The touch panel however should be equipped with a touchscreen panel (minimum size of 4.3 inches) designed to make user – unit interaction much easier by simplifying navigation between various screen menus.

Supervision Solutions

Different solutions of supervision to be available based on unit BMS card (Ethernet pCO Web or RS485 Carel/Modbus). These systems are used to manage the installation remotely. All the information on the system can be accessed via Internet connection. The online interface is to enable monitoring and complete configuration of the installation. For the remote control of multiple sites, special tools dedicated to centralized management, such as RemotePRO and RemoteValue should be used.

pCO Web

Solution for management and supervision of a single unit (if this incorporates the Ethernet pCO Web card).

BOSS

Solution for management and supervision of air-conditioning installations with up to three hundred (300) units. To be equipped with Integrated Hotspot Wi-Fi. BOSS should be able to offer advanced monitoring and maintenance functions that allow for the simple creation and management of zones and groups. BOSS should also allow for energy meters to be integrated to provide electricity consumption monitoring.

BOSS to be available in two versions:

- CPU device.

- CPU device with monitor, keyboard and screen.

For this option, each unit should be equipped with one (1) RS485 Carel/Modbus board.

PlantWatchPRO3

Solution designed for the monitoring of small and medium-size installations, capable to manage up to thirty (30) units. To be available in two versions: panel and wall. System to include: 7-inch display, buzzer for notifications, one (1) USB port, one (1) SD card slot for downloading reports, charging devices and applying service packs. For this option, each unit should be equipped with one (1) RS485 Carel/Modbus board.

Documentation

An operation and installation manual shall be delivered inside unit packaging. Documents such as product catalogue, Ecodesign information booklet, spare parts list, unit dimensional as well as wiring diagrams shall be accessible on a public website.

ηs,c=SEER kWhkWh×1002.50-icorrections

ηs,h=SCOP kWhkWh×1002.50-icorrections

WB: Wet Bulb Temperature (in oC).

DB: Dry Bulb Temperature (in oC).