General Description

Vertical-orientation packaged heat pump unit intended for indoor-use only and designed for optimum performance. Unit shall exceed minimum energy efficiency requirements set by EU Regulation 2016/2281 (Lot 21) valid as of January 2018. Unit shall be supplied in two (2) modules (outdoor and indoor module). Product shall be available in two arrangements; compact arrangement where both indoor and outdoor modules form a single structure and split-type arrangement where indoor and outdoor modules are to be installed separately. In case of split-type arrangement use, maximum equivalent cooling line length shall be at least fifty (50) meters long for installations where the outdoor module elevation is greater than indoor module elevation. In split-type arrangement applications where the outdoor unit elevation is lower than that of the indoor unit, maximum equivalent cooling line length shall be at least thirty (30) meters long. Unit shall be equipped with two (2) independent cooling circuits and a total of four (4) hermetic scroll-type compressors connected in tandem. Unit shall be equipped with plug type EC fans (electronically commutated motor with built-in variable speed control). Option to replace the indoor unit standard-fitted plug fan with a centrifugal belt-driven fan shall be available. For maximum adaptability, several assemblies should be available to meet numerous application-specific requirements. All units shall be factory tested.

| Ecodesign Requirements for Rooftops & Package Units (EU Regulation 2016/2281) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cooling | January 2018 |  | January 2021 |  |
|  | ηs,c % Primary Energy | SEER | ηs,c % Primary Energy | SEER |
| Cooling-only air to air package units | 117 | 3.00 | 138 | 3.53 |
| Heating | ηs,h % Primary Energy | SCOP | ηs,h % Primary Energy | SCOP |
| Heat pump air to air package units | 115 | 2.95 | 125 | 3.20 |

Directive, Standard and Regulation Compliance

Product to be Ecodesign 2018 ready, ISO 9001 and ISO 14001 certified. Product should comply with the following directives and standards:

- Machinery Directive 2006/42/EC (MD)

- Electromagnetic Compatibility Directive 2014/30/EU (EMC)

- Low Voltage Directive 2014/35/EU (LVD)

- Pressure Equipment Directive 2014/68/EU (Category 2) (PED)

- RoHS Directive 2011/65/EU (RoHS)

- Eco-design Directive 2009/125/EC (Ecodesign)

- Energy Labelling Directive 2010/30/EU (Eco-labelling)

- Harmonised Standard: EN 378-2:2012.

Unit Specification

Unit technical characteristics:

- Supply airflow: …. m3/h

- Extraction airflow: …. m3/h

- External static pressure, supply airflow: …. Pa

- External static pressure, extraction airflow: …. Pa

- Cooling Coil Capacity: …. kW

Assembly Options

Unit to be available in following configurations to match application-specific requirements:

Component Description

Outdoor Module

Casing

Outdoor module casing shall be made of galvanized steel metal sheets pre-painted with white colour RAL 7035 polyester paint. Module frame shall be self-supporting (i.e. able to bear module load with no plastic deformation).

Outdoor Air Circuit

Outdoor air circuit to be preferably equipped with direct-driven EC plug fans with built-in variable speed control and flow rate controller. Selection of fans and motors shall be such to ensure high component efficiency and consequently low energy consumption. Direct-driven EC plug fans are preferred over belt-driven centrifugal fans for several reasons:

- Plug fans eliminate friction losses during power transmission since they are direct-driven.

- Plug fans generally achieve greater rotor aeraulic efficiency (reactive blades with optimized profile). They are also able to run at very high operating pressures.

- EC fans generally achieve greater motor efficiency. Permanent magnet DC motors are activated using
motor-integrated electronic switches.

- EC fans are equipped with built-in variable speed drive to ensure a constant supply air flow rate, independent of filter clogging level.

- EC plug fans are able to accurately control the handled air flow on both constant- and variable- air volume systems by means of a differential pressure switch placed at fan intake.

Assembled-on-frame reusable air filters shall also be available. Outdoor module shall also be equipped with condensate drain pan to prevent the accumulation of water on mechanical and electrical components.

Cooling Circuit

Cooling circuit to be equipped with hermetic scroll-type compressors, assembled over anti-vibration mounts. Compressors shall be equipped with crankcase heater(s) to prevent compressor refrigerant condensation. A thermostatic expansion valve with external equalisation along with four-way cycle reversing valves shall also be fitted on unit cooling circuit. Compressor shall be equipped with suction accumulator, anti-acid dehydrating filter(s) and liquid receiver(s). Filling and service valves shall be available for compact arrangement units.

Electric Panel

Fully wired electric panel with panel insulation cover to prevent condensation. Electric panel to be protection IP55 certified. Electric panel to include power supply transformer (without neutral) and main ground connection. Electric panel to be equipped with compressor and fan motor contacts.

Protections

- High- and low- pressure switches.

- Compressor discharge temperature control.

- Non-return compressor valve.

- Main door switch.

- Magnetothermic protection switches for compressor power lines and fan motors.

- Control circuit automatic switch.

Indoor Module

Casing

Indoor module casing shall be made of galvanized steel metal sheets pre-painted with white colour RAL 7035 polyester paint. Module frame shall be self-supporting (i.e. able to bear module load with no plastic deformation).

Indoor Air Circuit

Coils shall be made of copper pipes mechanically expanded into aluminium fins. Fan sections to be equipped with 
direct-driven EC plug fans with built-in variable speed control and flow rate controller. The selection of fans and motors shall be such to ensure minimum energy consumption. Assembled-on-frame reusable air filters shall also be available. Indoor module shall also be equipped with condensate drain pan to prevent the accumulation of water on mechanical and electrical components.

Cooling Circuit

Cooling circuit shall feature thermostatic expansion valve(s) with external equalization.

Protections

Main door switch shall be mounted on indoor module.

Optional Component Description

Outdoor Module

Corrosion Protection

Following coil options shall be available to ensure component corrosion-resistance in all operating environments:

- Coil equipped with copper pipes mechanically expanded into copper fins.

- INERA® coil equipped with copper pipes and aluminium-alloy fins.

- Coil equipped with copper pipes mechanically expanded into aluminium fins with polyurethane and Blygold® coating.

Humidity Protection

- Tropicalised electric panel option.

- Tropicalised motor and fan options.

Installation

- Rubber anti-vibration mounts option.

- Oil separator option for applications where maximum equivalent cooling line length exceeds fifty (50) metres. Option only available for split-type arrangement units.

- Option to select supply air flow position: side supply by default, top-side supply available only for split-type arrangement units.

- Air coil protection grille option (not compatible with air filter).

- Option to add a gravimetric filter on return air side. Filter frame shall be removable. Frame should be able to be supplied separately for on-site assembly.

Acoustic Performance

Option to add compressor acoustic insulation covers.

Electric Panel

Energy meter option to allow for the monitoring of unit power consumption.

Indoor Module

Humidity

- Indoor air coil droplet eliminator. Recommended in applications where high air moisture content are common.

- Outdoor air intake droplet eliminator.

Corrosion

Following coil options shall be available to ensure component corrosion-resistance in all operating environments:

- Coil equipped with copper pipes mechanically expanded into copper fins.

- INERA® coil equipped with copper pipes and aluminium-alloy fins.

- Coil equipped with copper pipes mechanically expanded into aluminium fins with polyurethane and Blygold® coating.

- Stainless steel condensate drain pan option.

Heating

- Hot water auxiliary coil fitted with a three-way valve. Two options shall be available:

  - Primary Heating Coil in cooling-only units.

  - Auxiliary Heating Coil in reversible heat pump units.

Should the unit include a hot water coil and be equipped with free-cooling option, an anti-frost thermostat is to be installed if the unit operates at low ambient temperatures.

- Auxiliary Electrical Heaters: Air flow controller shall be included if an auxiliary electrical heater option is selected.

Indoor Air Quality

The following filter options shall be available:

- Supply air side filtration:

  - G4 class gravimetric filter.

  - G4 class gravimetric filter + creased opacimetric M6 to F9 class filters.

- Air quality probe to enable CO2 measuring.

Safety

- Supply and return fan soft starter option. This option shall only be available for belt-driven centrifugal fans. Option shall be compulsory for motors with a rated output equal or more than 15 kW.

- Differential pressure switch for the detection of filter clogging.

- Differential pressure switch for air flow control.

- Smoke detection station in accordance with NF S 61-961 standard requirements.

- Refrigerant leak detector option. This allows for the prompt identification of gas leakages, hence ensuring occupant safety. Installation of the device ensures F-GAS, EN378 and ASHRAE 15 standards compliance.

Installation

- Anti-vibration rubber mounts.

- Option to replace plug EC fans with centrifugal belt-driven fans.

- Configurable position of supply and/or return air side (several assemblies to choose from).

- Assemblies with mixing box for fresh air intake and free-cooling available.

Free-cooling

Units equipped with mixing box shall be able to function on free-cooling mode regulated by central electronic control. This function shall allow the exploitation of outdoor air conditions to reduce load on coil. Dampers shall be available to regulate the percentage of outdoor air flow (0% to 100% variation). Economizer control should be thermo-enthalpic i.e. economizer should work by comparing requested and outdoor air enthalpy and temperature values. This is the optimum solution as it takes climate variability into account. Thermal and enthalpic economizer control shall also be available as alternative options.

Control

Control system shall consist of an μPC MEDIUM control board, sensors, a pGD1 graphics terminal and, optionally, a user terminal. The described control system shall make use of an RS485 field-bus to manage additional unit components. A BMS card shall enable the connection of the control board to a centralized technical management system. The BMS card shall also manage the local connection between units through a pLAN network (μPC MEDIUM Local Area Network), allowing data and information to be exchanged between at least fifteen (15) units.

Minimum control functions:

- Selection of setpoint and operating mode: Heating/Cooling/Auto/Ventilation.

- Continuous control of system operating parameters.

- Display of sensor values.

- Compressor cycles monitoring.

- Management of defrost operation.

- Supply air temperature control.

- All-seasons operation via condensation and evaporation pressure control.

- Setpoint compensation based on ambient temperature.

- Hourly and weekly schedule options.

- Fire protection.

- Error diagnosis.

- Damper position control based on mixed air temperature and air quality sensor values.

- Auxiliary electric heater control.

- Hot water coil proportional ON/OFF control.

Terminal pGD1

Terminal to be fitted as standard on the electrical cabinet. It should be capable to provide control setting explanations in easy to understand English. Terminal should be able to:

- Carry out unit initial programming.

- Modify operating parameters.

- Switch the unit ON/OFF.

- Select operating mode and adjust setpoints.

- Display the variables controlled and sensor values measured.

- Display the current and past alarms.

TCO User Terminal (optional)

Terminal to be installed on the electrical cabinet (instead of the pGD1 terminal). In this case, remote connection of the pGD1 terminal should be possible. User terminal should be able to:

- Switch the unit ON/OFF.

- Select operating mode and adjust setpoints.

- Display: indoor air temperature and humidity, outdoor air temperature, supply air temperature, CO2 sensor readings  and damper control.

- Display alarm codes.

Electronic Control Medium (optional)

This controller is an electronic module equipped with a microprocessor comprised of a control board and a TCO. Optionally, this controller should have a terminal for pGD1 maintenance that facilitates the initial scheduling of the unit, the modification of the operating parameters and the description of the alarms produced.

Communication Options

Standard Controller

- TCO user terminal to be installed on electric panel (instead of pGD1 terminal).

- Remote control kit up to at least two hundred (200) meters with pGD1 terminal (pGD1 terminal + 2 TCONN bypass cards). Should this be used, installation of the TCO terminal on the electric panel shall be possible.

- Two to four ambient temperature probes with RS485 communication. By default, the controller shall include a negative temperature coefficient (NTC) probe.

- Ambient temperature and relative humidity probe with RS485 communication. Option shall be compulsory on units equipped with enthalpic or thermoenthalpic free-cooling mode.

- Air quality probe for CO2 measuring.

Electronic Control Medium (optional)

- pGD1 terminal for unit maintenance.

- Remote control kit up to at least two hundred (200) meters with pGD1 terminal (pGD1 terminal + 2 TCONN
bypass cards).

- Return or ambient air temperature probe connected to board.

- Mixing temperature probe: compulsory to manage of free-cooling mode operation.

Communication Protocols

Electronic Control Mediums shall allow for the connection to a centralised technical management system by using a specific BMS card for some of the following communication protocols:

- RS485 serial cards for network communication with protocols: Carel, Modbus, LonWorks®, BACnetTM MSTP and Konnex.

- Ethernet pCO Web cards for network communication with protocols: Modbus TCP/IP, BACnetTM Ethernet, TCP/IP, SNMP V1-2-3, FTP and HTTP.

Supervision solutions

Different supervision solutions to be available based on application requirements.

pCO Web

Solution for management and supervision of a single unit (if this incorporates the Ethernet pCO Web card).

PlantWatchPRO3

Solution designed for the monitoring of small and medium-size installations, capable to manage up to thirty (30) units. To be available in two versions: panel and wall. System to include: 7-inch display, buzzer for notifications, one (1) USB port, one (1) SD card slot for downloading reports, charging devices and applying service packs. For this option, each unit should be equipped with one (1) RS485 Carel/Modbus board.

PlantVisorPRO2

Solution designed for the management and supervision of HVAC installations with up to three hundred (300) units. System to be able to perform advanced monitoring and maintenance functions such as assigning units to groups which simplify the management of the installation. System shall allow for the integration of energy meters to monitor HVAC system power consumption. System to be available in two (2) versions:

- Box-version: arrangement to include system central processing unit (CPU) and, optionally, monitor and keyboard.

- Touch-version: arrangement to include system CPU and touchscreen.

These systems are used to manage the installation remotely. All the information on the system can be accessed via Internet connection. The online interface is to enable monitoring and complete configuration of the installation. For the remote control of multiple sites, special tools dedicated to centralized management, such as RemotePRO and RemoteValue should be used.

ηs,c=SEER kWhkWh×1002.50-icorrections

ηs,h=SCOP kWhkWh×1002.50-icorrections