General Description

Packaged rooftop unit consisting of autonomous, compact air to air units for the treatment of indoor air. Rooftop unit to be available in two (2) configurations to allow both cooling-only and reversible heat pump operation. Unit should also be available in several arrangements to fit all duct connection directional requirements. Unit should be designed for optimum part-load performance achieving the highest levels of seasonal efficiency and exceeding the minimum requirements set by EU Regulation 2016/2281 (Lot 21).  Unit should feature mono-block lightweight construction designed specifically to ensure easy installation and unit maintenance. Product should be equipped with the latest HVAC technological innovations featuring multi-scroll compressors, electronic expansion valves, electronically commutated (EC) motors with built-in variable speed control as well as auto-adaptive microprocessor control system. For maximum adaptability, several options should be available including exhaust air energy recovery sections, economizers, indoor air quality management systems and auxiliary heating modules.

| Ecodesign Requirements for Rooftops & Package Units (EU Regulation 2016/2281) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cooling | January 2018 |  | January 2021 |  |
|  | ηs,c % Primary Energy | SEER | ηs,c % Primary Energy | SEER |
| Cooling-only air to air rooftop units | 117 | 3.00 | 138 | 3.53 |
| Heating | ηs,h % Primary Energy | SCOP | ηs,h % Primary Energy | SCOP |
| Heat pump air to air rooftop units | 115 | 2.95 | 125 | 3.20 |

Unit Operating Limits

Unit should meet the following minimum operating limit requirements:

| Cooling Operation |  |  | Heat Pump Operation |  |  |
| --- | --- | --- | --- | --- | --- |
| Indoor Zone | Air Temperature |  | Indoor Zone | Air Temperature |  |
|  | Dry-Bulb | Wet-Bulb |  | Dry-Bulb | Wet-Bulb |
| Minimum Temperature | 18 oC | 13 oC | Minimum Temperature | 10 oC | - |
| Maximum Temperature | 35 oC | 24 oC | Maximum Temperature | 27 oC | - |
| Outdoor Zone | Air Temperature |  | Outdoor Zone | Air Temperature |  |
|  | Dry-Bulb | Wet-Bulb |  | Dry-Bulb | Wet-Bulb |
| Minimum Temperature | 10 oC | - | Minimum Temperature | -10 oC | -11 oC |
| Maximum Temperature | 52 oC | - | Maximum Temperature | 22 oC | 18 oC |
| Operating Mode |  |  | Minimum Outdoor Air Temperature |  |  |
| No compressor running & Free cooling mode |  |  | -20 oC |  |  |
| No compressor running & Electric heaters only mode |  |  | -20 oC |  |  |
| No compressor running & Hot water coil only mode |  |  | -20 oC |  |  |
| No compressor running & Gas burner only mode |  |  | -20 oC |  |  |

Directive, Standard and Regulation Compliance

Product to be Ecodesign 2021 ready, ISO 9001, ISO 14001, ISO 27001, ISO 50001, OHSAS 18001, SA 8000 and Eurovent certified. Product to be CE labelled. Product should comply with the following directives and standards:

- Machinery Directive: 2006/42/EC.

- Low Voltage Directive: 2014/35/EU.

- Electromagnetic Compatibility Directive: 2014/30/EU.

- Pressure Equipment Directive: 2014/68/EU.

- Safety of Machinery Directive, Electrical Equipment of Machines, General Requirements: EN 60204-1.

- Radiated Electromagnetic Emissions Directive: IEC 61000-3-3.

- Directed Electromagnetic Emissions Directive: IEC 61000-6-4.

- Electromagnetic Immunity Directive: IEC 61000-6-2.

Efficiency

All units shall be at least Eurovent Efficiency Class A certified. Efficiency calculations are to be conducted at full load conditions according to EN 14511-2018 standard requirements.

Unit Specification

Unit technical characteristics:

- Supply airflow: …. m3/h

- Extraction airflow: …. m3/h

- External static pressure, supply airflow: …. Pa

- External static pressure, extraction airflow: …. Pa

- Cooling Coil Capacity: …. kW

- Maximum coil velocity: …. m/s

Component Description

Casing

Supply unit shall have double-skin sandwich panels with a minimum thickness of 30 mm to minimize heat transfer between conditioned and ambient air. Sandwich panels shall be A1 Flame-Retardant Euroclass certified. Glass wool insulation shall be used with a minimum density of 30 kg/m3. Sandwich panels shall be made of 160 gr/m2 zinc-coated galvanized steel sheets. Outer sheet panel shall be powder-coated and corrosion-resistant. Product shall be subjected to 500-hour salt spraying test to verify corrosion-resistance properties. All panels shall be constructed in a manner that allows for their easy removal.

Filters

G4 type pleated filter placed before indoor unit coil. Filter shall be placed on sliding rail for easy removal and replacement.

The following filter options shall also be available:

- 50 mm, M1 Fire-Retardant certified, metal framed G4 pleated filter.

- 50 mm, M1 Fire-Retardant certified, metal framed F7 pleated filter.

- 50 mm + 50 mm, M1 Fire-Retardant certified, metal framed G4 + M6 pleated filters.

- 50 mm + 50 mm, M1 Fire-Retardant certified, metal framed G4 + F7 pleated filters.

Optionally the unit should be equipped with a differential pressure switch which shall stop the unit and display an alarm when the detected pressure drop in filters reaches a pre-determined critical value.

Coils

Coils are to be made of grooved copper pipes mechanically expanded into aluminium fins. All coils are to be tested against leakage in a water pool under 30 bar of pressurized air conditions following manufacturing. Coils shall feature interlaced (intertwined) structure on dual-circuit units to allow for reliable and efficient operation when only one cooling circuit is operating. To increase coil UV- and corrosion- resistance, indoor and outdoor unit coil aluminium fins should be able to be coated with polyurethane (upon request).

Drain Pan

Sloped drain pan to be fitted under all indoor coils. Drain pan to be made of minimum 304-grade stainless steel with the capacity to be dismantled through a sliding mechanism for easy service. Pan to be insulated on bottom side. A siphon shall be supplied by the manufacturer designed to drain accumulated water.

Cooling Circuit

R410A scroll compressors shall be used in unit cooling circuits. Electronic expansion valves shall also be used for better performance and safety. An electric crankcase heater shall be used on each compressor. Insulation shall be applied to compressor jackets to prevent freezing of the oil inside the compressor. An oil sight glass, filter drier, pressure and temperature sensors and high-pressure switch shall be installed on each cooling circuit. Rubber support blocks shall be used under the compressors to prevent vibration. During transportation, compressor anchoring units shall be used to prevent damage on copper piping of the cooling circuit. Units shall be equipped with either one (1) or two (2) independent cooling circuits. Single cooling circuits to be equipped with either fixed-speed or inverter compressor to achieve high seasonal energy efficiency. In applications where accurate unit response to load variation is required, inverter compressors shall be used to prevent consecutive ON/OFF compressor cycles, thus increasing the reliability of the cooling system and ensuring longer unit operating life. Double cooling circuits to be equipped with four (4) fixed-speed compressors.

Defrost Operation

Heat pump units operating in low ambient temperatures shall be able to perform a defrost operation controlled by an automatic adaptive algorithm taken from the controller to prevent frost on coils on the outdoor unit side. To prevent ice accumulation on the base of outdoor unit coil, coils shall be sloped for effective water drainage. An electric heater shall also be installed on the coil base.

Supply Fan

Supply fan(s) shall be of plug type equipped with EC motors (electronically commutated motors with built-in variable speed control) of minimum IE4 motor efficiency, IP54 protection and B insulation class. EC motors allow for the automatic regulation of air flow rate enabling reduced power consumption. Manual adjustment of air flow shall be performed by using unit controller. Fans shall be mounted on sliding rails and should be removable (outwards) through a guide for easy servicing. Fan operating mode shall be adjustable; the user may choose between a constant air volume (CAV) setting for fan operation with no duct pressure loss influence or a variable air volume (VAV) setting driven by indoor temperature variation. The unit shall also be equipped with a pressure sensor which shall stop the unit and produce an alarm in case of fan failure.

Return Fan

Return fan(s) should optionally be of plug type equipped with EC motors of IE4 motor efficiency class. Return fan(s) should work in series with supply air fan(s), compensating for total air duct pressure drop. Return fan(s) shall be mounted on sliding rails to allow for easy servicing. Should return fan(s) be included, an additional damper on the exhaust side of the unit shall exist for venting excess air. Additionally, a building pressure control option may be selected so that building air pressure may be adjusted by means of a controller led by a room pressure sensor. This feature is appropriate for applications where precise room pressure control is required.

Condenser Fan

Condenser fans shall be of direct-driven axial type. Fan protection grill to be fitted over fans, made of composite material resistant to corrosion. Fan motors shall be three-phased, having two (2) speed settings. Fans to have a minimum of IP54 protection and B insulation class rating with integrated overload protection.

Sensor

For effective room, ambient, supply and return air temperature control sensors are to be provided.

Economizer

Rooftops should be able to be equipped with economizer section consisting of two (2) fresh and return air dampers driven by appropriately-sized motors to allow for exploitation of favourable outdoor air conditions. With proper use of the economizer, coil capacity may be reduced. Economizer control should be either thermostatic or enthalpic; for thermostatic economizer control ambient and indoor temperature sensors are to be included whilst for enthalpic control humidity sensors need also be included. Damper frames and blades shall be made of aluminium and damper leakage class shall
be at least Class 2. Damper motor shall be of spring return type tso that dampers may automatically shut in case of 
power failure. Economizer shall be supplied with a hood to prevent the ingress of rainwater and a wire-fence to prevent the entry of miscellaneous objects. Economizer shall be able to provide free cooling automatically by adjusting the position of the dampers based on indoor cooling load requirements. This function is only possible when ambient air temperature is sufficiently low. By means of a CO2 sensor, unit should be able to control dampers automatically to preserve indoor air quality.

Control Panel/Human Machine Interface (HMI)

A power switch shall be installed on the control panel of the unit. For safety, unit panel doors should not be able to open until power switch is turned off. Cables on control panel shall be colour-coded and enumerated. Rooftop unit casing shall be fitted with IP68 protection class unions for all cable inputs and outputs. Unit controller shall manage cooling cycles to provide thermal comfort and maximize energy efficiency. Each unit shall be equipped with a microprocessor-controlled LCD display with a touch-sensitive colour screen that should be able to be programmed to configure all system parameters. This HMI shall be IP65 protection class certified and be equipped with an external cover for protection. Unit controller shall be remotely accessible via an Ethernet cable connection. Various functions such as weekly/daily/hourly scheduling, control over two (2) indoor sensors, master/slave control of up to six (6) units and night operation mode amongst others shall be available on controller menu.

Barometric Exhaust

Unit shall be equipped with barometric exhaust dampers made of aluminium blades. Barometric dampers are to be shut by gravity pull; the function of the dampers being the protection of the exhaust air side from rainwater and the discharge of pressure build-up.

Power Exhaust Fan

An axial exhaust fan shall be mounted on exhaust air side to enable excessive pressure build-up relief when fresh air rate exceeds a certain pre-defined value.

Electric Heater

Unit shall be equipped with a factory-installed and tested multi-stage electric heater. Electric heaters shall have a total of four (4) protection temperature switches; two (2) of which may be reset manually and two (2) which may be reset automatically. Electric heaters shall be switched on automatically during defrost operation.

Hot Water Coil

Unit shall be equipped with a hot water coil fitted with a 3-way valve. Hot water coils shall be switched on automatically during defrost operation. To simplify coil servicing, hot water coils shall be fitted with shut-off valves. Control of the regulating 3-way valve shall be applied according to supply air temperature requirements. 3-way valve should be fully modulated by unit central control system (0-10 V). A frost protection thermostat shall be installed on hot water coil.

Natural Gas Heater

Unit shall be equipped with a condensing-type, highly efficient natural gas burner with virtually zero CO and Class 5 NOx emissions. Capacity control of the natural gas heater shall be proportional with a 0-10 V signal. Burner combustion chamber and heat exchangers shall be made of AISI 441 stainless steel. For safety, natural gas heaters shall be equipped with a manual reset thermostat, ignition and flame detecting electrodes, flame ionization control and electronic ignition device.

Rotary Heat Recovery

Rotary heat wheels shall be used to enable the recovery of energy from the return air stream. Rotary heat wheels to be of either enthalpic- or sorption- type. The thermodynamic performance of all rotary heat wheels to be Eurovent certified. The housing module of the rotary heat recovery system shall be delivered separately. Module is to be connected directly to the unit, on-site, with manufacturer-provided connection apparatus without the use of any connecting ducts. The section between the wheel and the unit on the fresh air side shall be insulated by means of a 30 mm double wall. A single G4 filter shall be placed on fresh air inlet for the protection of the rotary heat wheel.

Thermodynamic Heat Recovery (THR)

For the utilization of return air stream energy, rooftop units shall be equipped with an additional cooling circuit equipped with a heat pump consisting of two (2) DX coils, one (1) placed at the exhaust air side and one (1) placed in front of the evaporator coil, a compressor and an expansion valve. Indicative schematic diagram of a rooftop unit equipped with thermodynamic heat recovery shown below:

Roofcurb

Unit to be equipped with a roofcurb that is capable to bear the weight of the unit.

Room Thermostat

A programmable room thermostat with an LCD display shall be provided to control unit operation remotely (ON/OFF switch, temperature control, mode selection, etc.).

Building Management System Communication

Unit shall be able to be equipped with the following Building Management System communications:

- JBus communication card.

- BACnet communication card.

- LonWorks communication card.

Safety

Unit shall stop operating and display an alarm under the following conditions:

- Should return air temperature measured by fire thermostat exceed a pre-determined value.

- Should filter pressure drop measured by differential pressure switch exceed a pre-determined value.

- Should smoke be detected in return air duct by smoke detection device.

Duct Connection

Unit should allow for the bottom, top and side connection of ducts by means of a supply and return air side plenum.

Documentation

Operation and installation manual shall be delivered inside unit packaging. Documents such as product catalogue, Ecodesign information booklet, operation and installation manual, spare parts list, dimensional as well as wiring diagrams shall be accessible on Internet.

Handling/Transportation

For easy on-site handling, unit base shall have sufficient space for the use of a forklift and/or lifting ropes. Unit shall be wrapped in nylon sheets for protection against ambient conditions during transportation and storage.

ηs,c=SEER kWhkWh×1002.50-icorrections

ηs,h=SCOP kWhkWh×1002.50-icorrections