Product specifications in italic shall be considered as key requirements.

SYSTEM DESCRIPTION

Factory assembled, air to water high-temperature monoblock heat pump utilizing scroll compressors, fixed-speed fans and optional hydronic pump module. The unit shall include all necessary wiring, piping, charge of R407C refrigerant, microprocessor controls and user display.

The unit shall have small footprint and a low height, allowing it to blend in with any architectural style. It shall be enclosed by easily removable panels, covering all components (except condensers and fans).

The high-temperature heat pumps shall incorporate the latest technological features:

- scroll compressors with vapour injection

- low-noise fans made of a composite material

- auto-adaptative microprocessor control

- electronic expansion valve

The unit may be equipped with a hydronic module that is integrated into the unit chassis, limiting the installation time

Note: Hydronic pump module shall be available with fixed-speed pump (for sizes 14 - 19KW)  and variable-speed driven pump (for sizes 22-105KW) and include all the necessary components as described in hydronic module option.

QUALITY ASSURANCE

Unit shall be rated in accordance with EN14511-3 Standard, latest revision and unit performances shall be certified by independent Eurovent certification body. Unit without independent Eurovent certification shall be excluded.

Unit construction shall comply with European directives:

- Commission Regulation (EU) N° 813/2013 implementing Directive 2009/125/EC of the European Parliament and of the Council with regard to Eco-design requirements for space heaters and combination heaters

- Commission regulation (EU) N°327/2011 implementing Directive 2009/125/EC with regards to Eco-design requirements for industrial fans.

- Commission regulation (EU) N°640/2009 implementing Directive 2009/125/EC with regards to Eco-design requirements for electric motors.

- Pressurized equipment directive (PED) 97/23/EC.

- Machinery directive 2006/42/EC, modified.

- Low voltage directive 2006/95/EC, modified.

- Electromagnetic compatibility directive 2014/30/EC, modified, and the applicable recommendations of European standards.

- Machine safety: electrical equipment in machines, general requirements, EN 60204-1.

Unit shall be manufactured in a facility registered to ISO 9001 Manufacturing Quality Standard and to ISO 14001 Environmental Management System. Unit shall be tested at the factory.

DESIGN PERFORMANCE DATA

Unit shall be certified by Eurovent independent body (mandatory) and comply with the following technical features:

- Heating Capacity (kW): ………..*

- SCOP according to EN14825: 3 2013 (kWh / kWh): ………..(average climate zone and water temperature  30οC/35oC)

- SCOP according to EN14825: 3 2013 (kWh / kWh): ………..(average climate zone and water temperature  47οC/55oC)

- Refrigerant type: R-407C

- Compressor type: Scroll

- Evaporator Pressure Drop (kPa): ......

- Number of compressors ……

- Maximum leaving water temperature: 65 (° C)

- Sound power level at full load (dB(A)): ……

- Sound pressure level 10m according to ISO 4871 (dB (A)): ……

- Refrigerant amount : ...... .. kg (. ... Kg / kW)

- Dimensions, length x depth x height (mm): …… x …… x ……

- Unit operating weight: ….. kg

*Operating Conditions:

- Hot water inlet / outlet temperature (° C): ……..

- Ambient temperature (° C) in heating mode: ……..οC DB (RH 87%)

UNIT CONSTRUCTION

- Frame shall be of heavy-gage, painted galvanized steel painted in oven-baked polyester powder paint (light grey, RAL7035).

- Electrical Cabinet shall be galvanized steel casing painted in oven-baked polyester powder paint (light grey, RAL7035).

COMPRESSOR ASSEMBLY

- Fully hermetic scroll type compressors with vapor injection each equipped with:

- Two-pole electric motor (Direct on line 230 or 400V depending on size, 2900rpm at 50Hz) cooled by suction gas and protected by internal temperature sensors.

- Initial oil charge of synthetic polyolester oil.

- Integral oil level sight glass.

- Electric crankcase heater to minimize oil dilution and refrigerant migration.

- Electronic over temperature motor protection.

Low noise level and low vibration level shall be guaranteed by:

- Flexible anti-vibration mounts to isolate compressor assembly from unit chassis.

- Suction and discharge piping designed to prevent the transmission of vibrations to the unit chassis.

WATER HEAT EXCHANGER

- Brazed plate heat exchanger, direct expansion.

- Plate exchangers shall be made of AISI 316 L stainless steel, copper brazed types.

- Heat exchangers shall be thermally insulated with 19mm closed cell foam type insulation.

- Heat exchanger shall be tested and stamped in accordance with European PED 97/23/EC Code.

AIR HEAT EXCHANGER

- Unit shall be equipped  with vertical evaporator coils

- Protection grilles on anti-vibration mountings shall protect the heat exchanger against possible shocks.

- Coil shall be air-cooled cupper tube aluminium fins heat exchanger (Cu/Al).

FANS

- Low-noise latest-generation Flying Bird IV fans, made of a composite material providing more quiet by not generating intrusive low-frequency noise

- Rigid fan installation for reduced start-up noise.

REFRIGERANT

- HFC R407C refrigerant

REFRIGERANT CIRCUIT

Units shall operate with R-407C refrigerant.

The refrigerant circuit shall be leak-tight with:

- Brazed refrigerant connections for increased leaktightness.

- Reduction of leaks due to elimination of capillary tubes (TXVs).

- Verification of pressure transducers and temperature sensors without transferring refrigerant charge.

The electronic expansion device (EXV) allows operation at a lower condensing pressure (COP optimisation). Dynamic superheat management shall provide a better utilisation of the condenser surface.

Auto-adaptive control algorithm shall prevent excessive compressor cycling.

ELECTRIC FEATURES

Unit shall operate on:

  - 230V 1-phase or 400V 3-phase, 50 Hz +/-10% power supply with neutral (for sizes 14-19KW).

The unit shall provide simplified electrical connections, with:

- Single power supply point.

- Main disconnect switch with high trip capacity

- Transformer for safe 24 V control circuit supply included.

ELECTRONIC CONTROL

The electronic control system shall combine intelligence with operating simplicity.

The control shall constantly monitor all machine parameters and precisely manage the operation of compressors, expansion devices, fans and of the condenser water pump for optimum energy efficiency and energy management

Seven-day internal time schedule clock shall be available so as to permit unit on/off control and operation at a second set point.

Set point reset shall be based on the outside air temperature or the return water temperature or on the water heat exchanger delta T.

Master/slave control of two heat pumps operating in parallel shall be available with operating time equalisation and automatic change-over in case of a unit fault, as described in available options.

Unit Start/stop can be based on the outside air temperature.

The backlighted LCD interface shall include a manual control potentiometer to ensure legibility under any lighting conditions.

The information shall be displayed clearly in English, French, German, Italian and Spanish and  other languages.

The control navigation shall use intuitive tree-structure menus, similar to the Internet browers. They shall be user friendly and permit quick access to the principal operating parameters: number of compressors operating, suction/discharge pressure, compressor operating hours, set point, air temperature, entering/leaving water temperature.

As standard the unit shall include a board for the control of a boiler and four electric resistance heater stages.

Remote operating mode with volt-free contacts (standard)

A simple two-wire communication bus between the RS485 port of the high-temperature heat pumps and the Network shall be available for offering multiple remote control, monitoring and diagnostic possibilities.

The provider shall offer a vast choice of control products, specially designed to control, manage and supervise the operation of a heating system. The following functions shall be available:

- Start/stop: opening of this contact will shut down the heat pump.

- Dual set point: closing of this contact activates a second heating set point (example: unoccupied mode).

- Demand limit: closing of this contact limits the maximum heat pump capacity to a predefined value.

- User safety: this contact is connected in series with the water flow switch and can be used for any customer safety loop.

- Water pump control.

- Alert indication: this volt-free contact indicates the presence of a minor fault.

- Alarm indication: this volt-free contact indicates the presence of a major fault that has led to the shut-down of the refrigerant circuit.

Remote interface (accessory)

Remote interface shall allow access to the same menus as the unit interface and can be installed up to 300 m away. This accessory includes a box that can be mounted inside the building. The power supply is provided via a 220 V/24 V transformer supplied.

Free defrost

Free defrost shall be provided in order to eliminate a relatively small amount of frost that has formed on the surface of the coil. Contrary to the standard defrost session; in the case of the free defrost session the heat (energy) shall be absorbed from the air. When running the free defrost, fans shall be activated and compressors shall be turned off. The free defrost is most efficient when the outside air temperature is above 1°C.

OPERATING CHARACTERISTICS

The unit shall be able to operate in a wide range, at ambient temperatures of -20 ° C up to +40°C

The unit shall be able to produce leaving water temperature up to 65 ° C even in summer, when the outdoor temperature reaches up to 40°C.

WATER CIRCUIT

Water circuit shall be rated for 10 bars maximum working pressure.

OPTIONS

The following options can be fitted to the unit, as required.

Master/slave operation

- Two units connected by CCN shall cooperate to assure system water temperature.

- System’s water temperature shall be controlled either by outlet or inlet temperature

- The master unit shall be the only interface to control the operation of both chillers.

- Three balance modes: Disabled, only on failure, according to run times.

Hydronic module

- The hydronic module shall be integrated in the heat pump chassis without increasing its dimensions and shall include the following components:

  - Inverter water pump.

  - Air purge

  - Water pressure gause

  - Flow switch

  - Water drain

CCN to J-Bus gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a JBUS Local Area Network (JBUS, ModBUS). Field programming for customisation is possible.

CCN to Lon gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a LonWorks® Local Area Network (LON, i.e., LonWorks FT-10A ANSI/ EIA-709.1). Field programming shall be required.

BACnet

Unit shall be supplied with factory-installed two-directional high-speed communication using BACnet protocol.