Product specifications in italic shall be considered as key requirements.

SYSTEM DESCRIPTION

Factory assembled, air to water high-temperature monoblock heat pump utilizing scroll compressors, fixed-speed fans and optional hydronic pump module. The unit shall include all necessary wiring, piping, charge of R407C refrigerant, microprocessor controls and user display.

The unit shall have small footprint and a low height, allowing it to blend in with any architectural style. It shall be enclosed by easily removable panels, covering all components (except condensers and fans).

The high-temperature heat pumps shall incorporate the latest technological features:

- scroll compressors with vapour injection

- low-noise fans made of a composite material

- auto-adaptative microprocessor control

- electronic expansion valve

The unit may be equipped with a hydronic module that is integrated into the unit chassis, limiting the installation time

Note: Hydronic pump module shall be available with variable-speed driven pump and include all the necessary components as described in hydronic module option.

QUALITY ASSURANCE

Unit shall be rated in accordance with EN14511-3 Standard, latest revision and unit performances shall be certified by independent Eurovent certification body. Unit without independent Eurovent certification shall be excluded.

Unit construction shall comply with European directives:

- Commission Regulation (EU) N° 813/2013 implementing Directive 2009/125/EC of the European Parliament and of the Council with regard to Eco-design requirements for space heaters and combination heaters

- Commission regulation (EU) N°327/2011 implementing Directive 2009/125/EC with regards to Eco-design requirements for industrial fans.

- Commission regulation (EU) N°640/2009 implementing Directive 2009/125/EC with regards to Eco-design requirements for electric motors.

- Pressurized equipment directive (PED) 97/23/EC.

- Machinery directive 2006/42/EC, modified.

- Low voltage directive 2006/95/EC, modified.

- Electromagnetic compatibility directive 2014/30/EC, modified, and the applicable recommendations of European standards.

- Machine safety: electrical equipment in machines, general requirements, EN 60204-1.

Unit shall be manufactured in a facility registered to ISO 9001 Manufacturing Quality Standard and to ISO 14001 Environmental Management System. Unit shall be tested at the factory.

DESIGN PERFORMANCE DATA

Unit shall be certified by Eurovent independent body (mandatory) andl comply with the following technical features:

- Heating Capacity (kW): ………..*

- SCOP according to EN14825: 3 2013 (kWh / kWh): ………..(average climate zone and water temperature  30οC/35oC)

- SCOP according to EN14825: 3 2013 (kWh / kWh): ………..(average climate zone and water temperature  47οC/55oC)

- Refrigerant type: R-407C

- Compressor type: Scroll

- Evaporator Pressure Drop (kPa): ......

- Number of compressors ……

- Maximum leaving water temperature: 65 (° C)

- Sound power level at full load (dB(A)): ……

- Sound pressure level 10m according to ISO 4871 (dB (A)): ……

- Refrigerant amount : ...... .. kg (. ... Kg / kW)

- Dimensions, length x depth x height (mm): …… x …… x ……

- Unit operating weight: ….. kg

*Operating Conditions:

- Hot water inlet / outlet temperature (° C): ……..

- Ambient temperature (° C) in heating mode: ……..οC DB (RH 87%)

UNIT CONSTRUCTION

- Frame shall be of heavy-gage, painted galvanized steel painted in oven-baked polyester powder paint (light grey, RAL7035).

- Electrical Cabinet shall be galvanized steel casing painted in oven-baked polyester powder paint (light grey, RAL7035).

COMPRESSOR ASSEMBLY

- Fully hermetic scroll type compressors with vapor injection each equipped with:

- Two-pole electric motor (Direct on line 230 or 400V depending on size, 2900rpm at 50Hz) cooled by suction gas and protected by internal temperature sensors.

- Initial oil charge of synthetic polyolester oil.

- Integral oil level sight glass.

- Electric crankcase heater to minimize oil dilution and refrigerant migration.

- Electronic over temperature motor protection.

- Optional soft starter to minimize compressor starting current with phase loss protection.

Low noise level and low vibration level shall be guaranteed by:

- Flexible anti-vibration mounts to isolate compressor assembly from unit chassis.

- Suction and discharge piping designed to prevent the transmission of vibrations to the unit chassis.

- Optional acoustic compressor jacket.

WATER HEAT EXCHANGER

- Brazed plate heat exchanger, direct expansion.

- Plate exchangers shall be made of AISI 316 L stainless steel, copper brazed types.

- Heat exchangers shall be thermally insulated with 19mm closed cell foam type insulation.

- Heat exchanger shall be tested and stamped in accordance with European PED 97/23/EC Code.

AIR HEAT EXCHANGER

- Unit shall be equipped  with vertical evaporator coils

- Protection grilles on anti-vibration mountings shall protect the heat exchanger against possible shocks.

- Coil shall be air-cooled cupper tube aluminium fins heat exchanger (Cu/Al).

FANS

- Low-noise latest-generation Flying Bird IV fans, made of a composite material providing more quiet by not generating intrusive low-frequency noise

- Rigid fan installation for reduced start-up noise.

REFRIGERANT

- HFC R407C refrigerant

REFRIGERANT CIRCUIT

Units shall operate with R-407C refrigerant.

The refrigerant circuit shall be leak-tight with:

- Brazed refrigerant connections for increased leaktightness.

- Reduction of leaks due to elimination of capillary tubes (TXVs).

- Verification of pressure transducers and temperature sensors without transferring refrigerant charge.

The electronic expansion device (EXV) allows operation at a lower condensing pressure (COP optimisation). Dynamic superheat management shall provide a better utilisation of the condenser surface.

Auto-adaptive control algorithm shall prevent excessive compressor cycling.

ELECTRIC FEATURES

Unit shall operate on:

  - 230V 1-phase or 400V 3-phase, 50 Hz +/-10% power supply with neutral (for sizes 14-19KW).

  - 400V 3-phase, 50 Hz +/-10% power supply without neutral (for sizes 22-105KW).

The unit shall provide simplified electrical connections, with:

- Single power supply point.

- Main disconnect switch with high trip capacity (for sizes 19-105 KW).

- Transformer for safe 24 V control circuit supply included.

ELECTRONIC CONTROL

The Touch Pilot Control shall include advanced communication technology over Ethernet (IP), user-friendly and intuitive user interface with 4.3" colour touch screen shall provide the following features.

- Energy management

- Internal time schedule clock: Controls heat pump on/off times and operation at a second set-point

- Set-point offset based on the outside air temperature

- Master/slave control of two heat pumps operating in parallel with operating time equalisation and automatic change-over in case of a unit fault.

- Integrated advanced communication features

- Night mode: Capacity and fan speed limitation for reduced noise level

- For units with hydraulic module: Water pressure display and water flow rate calculation

- Easy and high-speed communication technology over Ethernet (IP) to a building management system

- Access to multiple unit parameters.

- For units without hydraulic module: 0-10V output shall be available for external variable speed pump controL

- 4.3’’ Touch Pilot user interface

- Intuitive and user-friendly 4.3 inch touch screen interface

- Concise and clear information shall be available in 6 languages (English, Spanish, French, German, Italian and a possibility to add a sixth one based on user’s preference)

- Complete menu, customised for different users (end user, service personnel or engineers).

- Capacity to add up to two (2) user e-mail addresses for the automatic submission of fault reports.

Remote management

Unit shall can be easily accessed with Touch Pilot control from the internet, using a PC with an Ethernet connection. This makes remote control quick and easy and offers significant advantages for service operations.

The unit shall be equipped with an RS485 serial port that offers multiple remote control, monitoring and diagnostic possibilities. The unit shall be also communicate with other building management systems via optional communication gateways.

A connection terminal allows remote control of the unit by wired cable as follows:

- Start/stop: Opening of this contact will shut down the unit

- Dual set-point: Closing of this contact activates a second set-point (example: unoccupied mode).

- Demand limit: Closing of this contact limits the maximum chiller capacity to a predefined value.

- Operation indication: This volt-free contact indicates that the chiller is operating (cooling load).

- Alarm indication: This volt-free contact indicates the presence of a major fault that has led to the shut-down of one or several refrigerant circuits.

Free defrost

Free defrost shall be provided in order to eliminate a relatively small amount of frost that has formed on the surface of the coil. Contrary to the standard defrost session; in the case of the free defrost session the heat (energy) shall be absorbed from the air. When running the free defrost, fans shall be activated and compressors shall be turned off. The free defrost is most efficient when the outside air temperature is above 1°C.

OPERATING CHARACTERISTICS

The unit shall be able to operate in a wide range, at ambient temperatures of -20 ° C up to +40°C

The unit shall be able to produce leaving water temperature up to 65 ° C even in summer, when the outdoor temperature reaches up to 40°C.

WATER CIRCUIT

Water circuit shall be rated for 10 bars maximum working pressure.

OPTIONS

The following options can be fitted to the unit, as required.

Corrosion protection

Fins made of pre-treated aluminium (polyurethane and epoxy) for improved corrosion resistance, recommended for moderate marine and urban environments

100Pa external static pressure on fans (for sizes 35-105KW)

Fans with maximum available pressure 100 Pa, for indoor unit installation with discharge air ducts

Low sound level operation (for sizes 22-105KW)

Aesthetic and sound absorbing compressor enclosure reduces noise level by 1 to 2 dB(A)

Super low sound level operation (for sizes 22-105KW)

Aesthetic and sound absorbing compressor enclosure associated with low-speed fans reduces noise level by 6 to 7 dB(A)

Compressor soft starter (for sizes 22-105KW)

Electronic starter on each compressor to reduce the start-up current.

Water piping cable heaters for hydronic module (for sizes 22-105KW)

The frost protection of the heat pump water piping is guaranteed down to -20oC by automatically energized heaters and pump cycling.

Master/slave operation

- Two units connected by CCN shall cooperate to assure system water temperature.

- System’s water temperature shall be controlled either by outlet or inlet temperature

- The master unit shall be the only interface to control the operation of both chillers.

- Three balance modes: Disabled, only on failure, according to run times.

Hydronic module

- The hydronic module shall be integrated in the heat pump chassis without increasing its dimensions and shall include the following components:

  - Inverter driven circulator

  - A strainer

  - An air purge

  - Two drain valves

  - A pressure relief valve

  - One pressure transducer to measure the water system pressure

  - Flow switch

CCN to J-Bus gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a JBUS Local Area Network (JBUS, ModBUS). Field programming for customisation is possible.

CCN to Lon gateway

Unit shall be supplied with factory-installed two-directional communication board to interface the unit with a LonWorks® Local Area Network (LON, i.e., LonWorks FT-10A ANSI/ EIA-709.1). Field programming shall be required.

BACnet over IP

Unit shall be supplied with factory-installed two-directional high-speed communication using BACnet protocol.

Set point adjustment by 4-20mA signal.

Connections to allow a 4-20mA signal input.