General description

Water-cooled (61WG) liquid heat pump for indoor installation, equipped with scroll compressors, Pro-Dialog+ control and operating with R-410a refrigerant that has no effect on the ozone layer.

Quality assurance

Unit shall be rated in accordance with Eurovent standard.

Unit construction shall comply with European directives:

- Pressurised equipment directive (PED) 97/23/EC

- Machinery directive 2006/42/EC.

- Low voltage directive 2006/95/EC.

- Hazardous Substances in electrical and electronical equipment directive 2002/95/CE ((RoHS)

- Waste Electrical & Electronic Equipment directive 2002/96/EC (WEEE)

- Electromagnetic compatibility directive 2004/108/EC, modified, and the applicable recommendations of European standards

- Directive 2005/32/EC with regard to ecodesign requirements for electric motors

Unit shall be designed, manufactured and tested in a facility with a quality management system certified ISO 9001 and environmental management system ISO 14001.

Unit shall be run tested at the factory. The development test site of the units shall be certified to the quality management system ISO 17025.

Design performance data

- Heating capacity (kW): ……

- Unit power input (kW): ……

- Evaporator entering/leaving water temperature (°C): … /

- Fluid type: …….

- Fluid flow rate (l/s): ……

- Evaporator pressure drops (kPa): ……

- Condenser entering/leaving water temperature (°C): ……

- Fluid type: …….

- Fluid flow rate (l/s): ……

- Condenser pressure drops (kPa): ……

- Sound power level at full load (dB(A)): ……

- Dimensions, length x depth x height (mm): … x … x

- Number of compressors

The unit shall be capable of starting with up from 7.5 °C up to 27 °C entering water temperature to the evaporator.

The unit shall be capable of starting with up from 15 °C up to 60 °C entering water temperature to the condenser. For a condenser with an entering temperature below 15 °C the use of a three way valve recommended.

The unit shall operate with condenser leaving water temperature from 20 °C.up to 65 °C.

The unit shall operate with evaporator leaving water temperature from 5 °C up to 20 °C.

(Carrier option 272) (geothermal application)

The unit can achieve high-temperature water production on the condenser side, with glycol solution on the evaporator side. This option can be used for Geothermal application and domestic hot-water production.

The unit shall be capable of starting with up from -2.5 °C up to 25 °C entering water temperature to the evaporator.

The unit shall be capable of starting with up from 15 °C up to 60 °C entering water temperature to the condenser. For a condenser with an entering leaving temperature below 15 °C the use of a three way valve recommended.

The unit shall operate with condenser leaving water temperature from 20 °C.up to 65 °C.

The unit shall operate with evaporator leaving water temperature from - 5 °C up to 20 °C.

The pressure control signal will ensure safe unit operation and maximised performance at low sourceside

water temperatures.

Frame

Chassis and cabinet made of galvanised sheet steel. Painted in oven-baked polyester powder paint in light grey colour (RAL 7035). Removable side and rear panels.

The unit shall have water connections at the top/back.

Compressor

- Unit will have Hermetic scroll compressor driven by direct drive of 2-pole electric motor.

- Motor will have been cooled by a  suction gas , passing over the motor windings.

- Motor will have been overload protection through an internal thermostat.

- The compressors will have been installed and fixed with anti-vibration mounts to minimize vibration transfer within the unit .

- Compressors will have polyolester synthetic oil charge, and oil level sight glass.

Dangerous compressor cycles are reduced to six per hour.

(Carrier option 25) Consists of an electronic soft-starter per compressor. This permits optimizing the start-up current, and reducing nuisance cut-outs due to current surges in the electrical system at start-up.

(Carrier option 257) Compressor and oil separator sub-assembly and refrigerant gas suction line shall be acoustically insulated

Evaporator

The evaporator will be stainless steel direct-expansion plate heat exchanger with Victaulic connections. The  max. water-side operating pressure is 1000 kpa.

Condenser

The condenser will be stainless steel plate heat exchanger with Victaulic connections. From size 61WG 50 upwards the condenser has two interlaced independent refrigerant circuits. The  max. water-side operating pressure is 1000 kpa.

(Carrier option 86) There is an additional thermal insulation in the condenser , optimized for heating applications.

Refrigerant circuit

Each circuit will include:

- One or two compressors

- Liquid linevalve,

- Moisture sight glass.

- Filter drier.

- Thermostatic expansion device,

- High and low pressure transducers.

- Manuallyreset high pressure switch,

- R-410a refrigerant charge.

Control and power circuit control box

- The unit shall operate with 400 V-3 ph-50 Hz (400 V ± 10%) without neutral and it shall only have one connection point

- The main control panel shall be protected by a glass panel and shall only be opened with a special tool.

- The unit control circuit voltage shall be 24 V maximum, supplied by a factory-installed transformer. The compressor shall offer quick keyed electrical connection

- The control menus shall permit direct access do all unit data including the history of possible faults.

(Carrier option 70F) The handle of the electrical disconnect switch is on the outside of the unit

Evaporator hydronic module

The original pumps that are factory-installed in these units have motors with efficiency class IE2.

The hydronic module is located in the upper unit section.

There are two hydronic module available:

(Carrier option Option 116T): Evaporator hydronic module equipped with low pressure fixedspeed pump, drain valve, air vent and pressure sensors.

(Carrier option Option 116V): Evaporator hydronic module equipped with high-pressure variable-speed pump, drain valve, air vent and pressure sensors.:

(Carrier option Option 293) :The hydronic module includes screen filter, expansion tank and safety valve integrated in the evaporator hydronic module.

Note: Units without hydronic module (standard): water flow switch installed as standard .

Condenser hydronic module

The original pumps that are factory-installed in these units have motors with efficiency class IE2.

The hydronic module is located in the upper unit section.

(Carrier option Option 270T): Condenser hydronic module equipped with low pressure fixedspeed pump, drain valve, air vent and pressure sensors.

(Carrier option Option 270V): Condenser hydronic module equipped with high-pressure variable-speed pump, drain valve, air vent and pressure sensors.

(Carrier option Option 293A) :The hydronic module includes screen filter, expansion tank and safety valve integrated in the condenser hydronic module.

Control system

Pro-Dialog+ is a numerical control that combines intelligence with operating simplicity. Depending on the

options used, the unit manages the operation of compressors, evaporaor and condenser water pumps and

fans (drycooler).

A patented auto-adaptive algorithm will optimise the condensing pressure at part load to reduce compressor

load and ensure perfect supply for the evaporator with liquid refrigerant. The algorithm controls the operation of the variable-speed condenser water pump and the fans (drycooler)

Pro-Dialog+ automatically resets the chilled-water temperature setpoint based on the outside air temperature or the return water temperature. The control can also operate on a second setpoint (example: unoccupied mode).

- The Pro-Dialog+ interface includes five keys that permit navigation via intuitive tree-structure menus. Access to the information is very quick.

- This new backlit LCD interface includes control by a contrast potiometer for optimised visibility in all lighting conditions.

- The information is clearly displayed in English, French,German, Italian and Spanish (for other languages please consult Carrier Service).

- The Pro-Dialog+ navigation uses intuitive tree-structure menus, similar to the Internet navigators. The menus are user-friendly and permit quick access to the principal operating parameters: number of compressors operating, suction/discharge pressure, compressor operating hours, setpoint, temperatures.

- (Carrier option 148B) A two-directional communication board shall allows plug and play interfacing of the machine with any BMS using the J-Bus protocol.

- (Carrier option 148C) A two-directional communication board shall allows plug and play interfacing of the machine with any BMS using the BacNet protocol

- (Carrier option 148D) A two-directional communication board shall allows plug and play interfacing of the machine with any BMS using the LonTalk protocol

(Carrier option 275)Remote chiller management

Pro-Dialog+ permits control and monitoring of the unit using a wired interface:

- Start/stop

- Operating mode selection: cooling or heating

- Demand limit

- Dual setpoint

- User safety loop.

The control remotely reports any problem.

The CCN clock board connection offers other control possibilities:

Two independent time schedules to control:

- Unit start/stop

- Operation at a second chilled-water setpoint

- Operation of two units in parallel (master/slave function), and remote control via a communication bus.

Note: For units without hydronic module (standard) a 0-10 V output is available to control a three-way valve or a variablespeed condenser water pump.

Safeties

A patented auto-adaptive algorithm controls compressor operation and permanently adapts to the

system charac-teristics (water loop inertia). Dangerous compressor cycling is prevented.

Pro-Dialog+ permanently analyses the compressor suction and discharge pressures and temperatures. If an

abnormal situation is detected, the control reacts, e.g. by reducing the capacity. As a result the compressors always operate in their ideal temperature range and many unit shut-downs due to a fault can be prevented.

(Carrier option 58) Unit equipped with an additional field-installed leaving water temperature sensor, allowing master/slave operation of two units connected in parallel.

Master/slave operation

- Two units connected by CCN shall cooperate to assure system water temperature.

- The master unit shall be the only interface to control the operation of both chillers.

- Up to 5 possible water loop configuration (parallel, common or dedicated pumps, series…).

- Three balance modes: Disabled, only on failure, according to run times.

- Common pump management (external pump and units provided with flow switch only) or dedicated pump management (internal pump can be used).

Heating System Manager (Accessory)

Heating System Manager type A

Allows control of a non-reversible heating system that includes a 61WG heat pump and a single heat emitter type or a single comfort zone. For optimised energy efficiency the heat pump is controlled by a configurable system based on the outdoor weather temperature. The control box controls a supplementary electric heater or a standy-by boiler. The control box supplies power to the circulating pumps.

Heating System Manager type B

Allows control of a non-reversible heating system that includes a 61WG heat pump and two different heat emitter types and/or two independent comfort zones. For optimised energy efficiency the heat pump is controlled by a configurable system based on the outdoor weather temperature.The control box controls a supplementary electric heater or a standy-by boiler. The control box supplies power to the circulating pumps. Hot-water production can be permanent or programmable with a second setpoint at the heat pump and control of a switching valve.

Heating System Manager type C

Allows control of a non-reversible heating system that includes a 61WG heat pump and two different heat emitter types and/or two independent comfort zones. For optimised energy efficiency the heat pump is by a configurable system based on the outdoor weather temperature.The control box controls the heating and/or domestic hot-water production support from a district heating system. The control box supplies power to the circulating pumps. Hot-water production can be permanent or programmable with a second setpoint at the heat pump and control of a switching valve.