General Description

The plate heat exchanger consists of heat exchange plates, the frame, the clip elements and input / output ports.

The plates are made of profiled metal sheets with grooves designed this way in order to achieve maximum heat transfer. Each plate has a plastic gasket of synthetic rubber that seals the liquid between the two plates. The liquid flows through a narrow space between the plates and the heat is transferred from the surface of the plates.

Quality Assurance

The exchanger plant and the construction of the exchanger itself will comply with the following European regulations:

- Directive pressure equipment (PED) 97/23/EC

- Sanitary certification for use in drinking water installations, ΑCS

- Certified production line for exchangers manufacturing according to international quality assurance standards EN ISO 9001:2008

The heat exchanger will be manufactured in a factory with a certified environmental management system ISO 14001.

The heat exchanger will be manufactured in a factory with Certified production line for exchangers manufacturing according to international work safety assurance standards for production areas  OHSAS 18001.

Exchanger Design

- Power of thermal exchange : 					                                   kW

- Selection of way of heat exchange (confluent or counterflow)

- Selection of type and quality of fluid

- Temperature inlet / outlet of primary & secondary	                                                °C

- Pressure operation of primary & secondary              	                                            bar ή kPa

- Pressure drop of primary & secondary                                                                        bar ή kPa

- Percentage of coverage of the required Power

- Margin of increase of the existing number plates for selected frame exchanger

- Frame and Ports

The frame is made of painted steel with colored finish dark blue, with possibility of selecting the type of input - output ports depending on the frame size. The frame retains the heat exchange plates together and they are fitted together with suitable rubber gasket. The basic frame sizes - (input / output) are the following:

- 10TE020+ (DN32) with maximum flow 19 m3/h

- 10TE040+ (DN32) with maximum flow 19 m3/h

- 10TE080+ (DN32) with maximum flow 19 m3/h

- 10TE070+ (DN50) with maximum flow 63 m3/h

- 10TE160+ (DN50) with maximum flow 63 m3/h

- 10TE260+ (DN50) with maximum flow 63 m3/h

- 10TE125+ (DN65) with maximum flow 80 m3/h

- 10TE180+ (DN65) with maximum flow 83 m3/h

- 10TE300+ (DN100) with maximum flow 108 m3/h

- 10TE450+ (DN100) with maximum flow 193 m3/h

- 10TE700+ (DN100) with maximum flow 280 m3/h

- 10TE400+ (DN150) with maximum flow 215 m3/h

- 10TE600+ (DN150) with maximum flow 355 m3/h

- 10TE900+ (DN150) with maximum flow 631 m3/h

- 10TE650+ (DN200) with maximum flow 334 m3/h

- 10TE990+ (DN200) with maximum flow 534 m3/h

The choice of orifice type depends on the specification set by designer and how this defines the type of connection. General types of orifices relative to the frame size is the following:

- Port tube type with orifice male thread end (DN32 to DN65)

- Port tube type with grooved end type Victaulic (DN32 to DN65)

- Port tube type with flange end (DN32 to DN65)

- Port socket type for flange without rubber fininshing (DN100 to DN200)

- Port socket type for flange with rubber fininshing (DN100 to DN200)

The relationship between frame and operational pressure is specified below:

- 10TE020+ (6/10/16/25 bar)

- 10TE040+ (6/10/16/25 bar)

- 10TE080+ (6/10/16/25 bar)

- 10TE070+ (6/10/16/25 bar)

- 10TE160+ (6/10/16/25 bar)

- 10TE260+ (10/16/25 bar)

- 10TE125+ (10/16 bar)

- 10TE180+ (10 bar)

- 10TE300+ (10/16/25 bar)

- 10TE450+ (10/16/25 bar)

- 10TE700+ (10/16/25 bar)

- 10TE400+ (10/16 bar)

- 10TE600+ (10/16 bar)

- 10TE900+ (10/16 bar)

- 10TE650+ (10/16 bar)

- 10TE990+ (10/16 bar)

Heat Exchange Plates

The plates are made of profiled metal sheets and grooved to form on their surface a "herringbone" pattern. They will carry at their ends lateral grooves for better support on the frame and will have sophisticated hexagonal profile for optimal plate-frame assembly. Plates may have a thickness of 0.4, 0.5 to 0.6 millimeters. Depending also from the size of the frame the above thicknesses can be categorized as follows:

-	0,4mm, (6/10 bar)

-	0,5mm, (6/10/16 bar)

-	0,6mm, (6/10/16/25 bar)

The exchange plates can be made out of stainless steel 304L category for refrigeration applications, for pure water or glycol or water with a chlorine content of up to 50 ppm at 50 ° C. It may be made of stainless steel 316L category for heating / cooling applications, for pure water or glycol, or water with a chlorine content of up to 250 ppm at 50 ° C. They can be made from stainless steel 254SMO category for heating / cooling applications with pure water or glycol or water with a chlorine content of up to 6000 ppm chloride ion at 50 ° C. Another available option is the titanium plates for heating / cooling applications, for pure water or glycol, or seawater (3,5% chlorides).

Gasket

The plastic gasket is made from synthetic rubber and is the joint system of the plate to the frame of the exchanger. It can be made of NBR for Heating / Cooling applications with temperature limit: -20 ° C + 110 ° C or EPDM for Heat / Cool applications and steam, unsuitable for applications with fluids or mixtures of hydrocarbons and mineral oils with temperature limit: - 20 ° C + 160 ° C or FPM suitable for many chemical and organic compounds, sulfuric acids and vegetable oils limit temperature: -20 ° C + 200 ° C.