DESCRIPTION OF THE SYSTEM

Multi-zone, multi-split, air-cooled, direct expansion system, with variable refrigerant flow working with refrigerant R410A, with heat recovery.

In general, this system shall consist of one or more interconnected outdoor units and several indoor units, on a single refrigerant three piping network.

The system shall operate as a heat pump, with the possibility of simultaneous operation in cooling or heating mode and the system's main characteristics are as follows:

- Extensive capacity of oudoor & indoor units.

An array of outdoor units consisting of 1 to 4 units, with a cooling capacity ranging from 25.2 kW (8 HP) to 180 kW (64 HP)

The number of connected indoor units in an array, through a single piping network, shall include up to 64 units of all types and sizes (more than 100 different models.) The total output of the indoor units can be from 30% to 130% of the total capacity of the system's outdoor units.

- Continuous heating during defrosting operation

The heat exchanger of each outdoor unit consists of two parts. Each section is defrosted separately from the second and in differential time. The defrosting is achieved by the heat transferred from the first  section to the second. With this technology heating is continued  with capacity at least 50%.

- Certificates

The manufacturing plant shall have manufacturing quality certification as per ISO 9001 and environmental management system as per ISO 14001.

The units shall be manufactured in accordance with the following European directives/ regulations:

- Directive 2004/108/EC relating to electromagnetic compatibility.

- Directive 2006/42/EC on machinery.

- Directive (PED) 97/23/EC on pressure equipment.

- OUTDOOR UNITS

All outdoor units shall be assembled at the plant; they shall be made of galvanized iron sheet with electrostatic painting, and shall consist of a separate part of compressors - exchangers.

The individual-main outdoor units shall range from 8 HP to 16 HP and performance shall be as follows:

| POWER | INDICATIVE TYPE | COOLING CAPAITY KW | HEATING CAPACITY KW |
| --- | --- | --- | --- |
| 8 HP | 38VF008T119010 | 25.2 | 27.0 |
| 10 HP | 38VF010T119010 | 28.0 | 31.5 |
| 12 HP | 38VF012T119010 | 33.5 | 37.5 |
| 14 HP | 38VF014T119010 | 40.0 | 40.0 |
| 16 HP | 38VF016T119010 | 45.0 | 45.0 |

Capacities shall be valid under the following operating conditions:

Cooling:	Indoor Temperature 27οC DB/19oC WB & Outdoor Temperature 35oC DB

Heating: 	Indoor Temperature 20οC DB/19oC WB & Outdoor Temperature 7oC DB/6oC WB

It shall be possible to interconnect the above individual & main units to forming a single cooling system, with two or three units, thus extending the efficiency of a system with an output of up to 64 HP.

An array of outdoor units can be consisting based on the highest performance (High efficiency combination)

The seasonal energy of efficiency of the systems, SEER for cooling, shall be as high, as follows:

SEER energy efficiency ratio for 8 HP to 12 HP units > 5.76

SEER energy efficiency ratio for 14 HP to 16 HP units > 5.59

All units shall be equipped with scroll DC inverter compressors.

The main outdoor 8HP, 10HP & 12HP units shall have one (1) DC inverter compressor, while the main outdoor units of 14HP, 16HP shall have two (2) DC inverter compressors.

Operating cycle

In an array of outdoor units, each outdoor unit of the array shall be able to operate as the main unit, and the main outdoor unit shall alternate cyclically in one operating period, to extend the lifetime of the overall system.

In the event of a fault in one of the outdoor units in the array, the system shall be capable of remaining operative, using the other outdoor units.

In the event of a fault in one of the compressors of the external unit, the system shall be capable of remaining operative, using the other compressor.

All outdoor units shall be equipped with their own power and control panel, access to the electrical panel shall be through a detachable metal panel.

The unit shall have three-phase power supply, including neutral and earthing; voltage: 400(380-415)Volts/50Hz.

The noise level of the outdoor units shall be low. The noise level shall be measured from a distance of 1m horizontally and 1.3 m above the base of an outdoor unit or an array of units, and shall not exceed the following limits (cooling mode):

| Outdoor Units | Sound pressure level dB(A) |
| --- | --- |
| 8 HP | 57.0 |
| 10 HP | 57.0 |
| 12 HP | 58.0 |
| 14 HP | 60.0 |
| 16 HP | 60.0 |

It shall be possible for the system to reduce the noise level (night mode) by reducing the system's capacity and outdoor fan speed.

The system shall operate under extreme outdoor environmental conditions both for cooling and for heating as follows:

- Cooling mode:	from -5οC to + 48οC DB

- Heating mode:	from -20οC to + 24οC DB

- Simultaneous cooling/heating mode: από –5°C έως + 24°C DB

- Expansion valves - EXV

Each outdoor unit shall be equipped with double electronic expansion valves EXV, with each EXV achieving 480 pulses for precise regulation of the refrigerant flow.

The outdoor units shall be equipped with multiple electromagnetic valves for precise temperature control.

- Precise oil control technology.

The oil control is based on five steps to ensure the safe level of oil in the outdoor unit and the compressor.

1st stage: separate lubrication inside the compressor.

2nd stage: separator high efficiency oil (separation efficiency up to 99%).

3rd stage: oil balancing technology between the compressors of the same outdoor unit.

4th stage: oil balancing technology between the outdoor units.

5th stage: intelligent oil-return system.

- Compressors

The individual outdoor units from 14 HP to 16HP shall include two (2) scroll DC inverter compressors, which shall change operation from 60Hz to 140 Hz.

The compressors shall start smoothly, to prevent voltage drops.

In case of failure of a compressor of an outdoor unit, the system can be continue the operation with the second compressor.

- Heat exchangers

The heat exchangers of the outdoor units shall be manufactured at the factory using specially configured high heat transfer coper tubes, suitable for R410A refrigerant, mechanically expandable to multiple aluminum fins.

The surface of the fins shall be covered by a blue hydrophilous layer that shall ensure protection from corrosion and better condensate diffusion.

- Fans

The fans shall be directly connected to high performance, impermeable and permanent lubrication, DC inverter motors.

The impellers of the fans shall be specially designed and manufactured to ensure minimal disturbance of the air flow between blades, as well as a low noise level.

Fan speed shall be controlled and regulated on the basis of the external unit load level and the pressure of the refrigerant.

The fans shall have available static pressure up to 20 Pa, which may be increased up to 60 Pa for outdoor units 8 HP, 10 HP, 12 HP and up to 40 Pa for outdoor units 14 HP, 16 HP(upon request).

- Safety devices

All outdoor units shall be equipped with the following safety devices:

High and low pressure sensors, fuse switches, automatic compressor motor overload fuse, compressor and fan motor overheating switch, oil chamber electrical resistors, restart cycle timer, temperature, suction pressure and compressor discharge sensors.

- Mode Switch MS equipment

For the simultaneous operation in cooling and heating mode, Mode Switchs MS are necessary to install.

The system checks the operation mode to cooling or heating of each or group of indoor units separately through

the MS. Each MS and depending on its type, has a corresponding number of electromagnetic valves for precise

control of refrigerant flow.

Ability to choose of different types of flow selectors:

Selectors for connecting a group of indoor units

Selectors for connecting multiple indoor units groups, with possibility of independent operation of each group

either in cooling or in heating mode.

It should be possible options as follow:

| indicative type | MSFT-01C-CM | MSFT-02C-CM | MSFT-04C-CM | MSFT-01C-CM | MSFT-02E-CM | MSFT-04E-CM |
| --- | --- | --- | --- | --- | --- | --- |
| Max. indoor unit groups | 1 | 2 | 4 | 6 | 1 | 1 |
| Max. number of each group indoor units | 4 | 4 | 4 | 4 | 1 | 1 |
| Max. number of all downstream indoor units | 4 Χ 1= 4 | 4 Χ 2 = 8 | 4 Χ 4 = 16 | 4 Χ 6= 24 | 1 | 1 |
| Max. capacity of each group indoor units Total capacity of all downstream indoor units | 16 | 16 | 16 | 16 | 20~28 | 40~56 |
| Total capacity of all downstream indoor units | ≤16 | ≤ 28 | ≤ 45 | ≤ 45 |  |  |

- Piping

It shall be possible for the system to have extended piping, specifically:

- Maximum equivalent distance from the outdoor unit to the most remote indoor unit:  200 m.

- Maximum equivalent distance between the first refrigerant piping connector (joint) and the most remote indoor unit: up to90 m.

- Maximum Piping length from MS to the downstream indoor unit of itself :40 m

- Maximum elevation difference between outdoor-indoor units: 110 m.

(70 m if the outdoor unit is at a higher position)

- Maximum elevation difference between indoor units: 30 m.

- Maximum length of refrigerant piping: 1,000 m.

The pipeline will be three pipes (gas-liquid-return gas) from the outdoor unit to the flow selector while after the selector and to the each internal network will be two pipes.

The thickness and quality of piping shall be suitable for R410A refrigerant, and in accordance with the manufacturer's manuals.

The refrigerant piping must be clean and nitrogen gas must be used during welding, in order to avoid oxidation inside the pipes.

- Installation of units in the project

The factory rules must be followed  when installing the units at the job site. The outdoor units must be installed in such a way as to allow easy access in case of maintenance or repair. There should be no obstacles on the front covers (of the electrical panel). All distances specified by the manufacturer and concerning the smooth operation of the units must be followed, and there must not be any obstacles at the fan exits.

If the units are interconnected in the form of an array, the pipes passing by the check points of the unit must be at a distance of at least 50 cm from the unit so as to allow any future repair work (e.g. replacement of a compressor).

INDOOR UNITS OF THE SYSTEM

The following different types of indoor units shall be available, depending on the use and site of installation:

- One-way ceiling cassette, capacity from 1.8 kW to 7.1 kW, in 7 sizes, ind. type 40VZ_H11200010

- Two-way ceiling cassette, capacity from 2.2kW to 7.1 kW, in 6 sizes, ind. type 40VT_H10200010

- Four-way ceiling cassette 60x60, capacity from 2.2 kW to 4.5 kW, in 4 sizes, ind. type 40VX_H11200010

- Four-way ceiling cassette, capacity from 2.8 kW to 14.0 kW, in 10 sizes, ind. type 40VK_H11200010

- Concealed ducted unit, low static pressure, capacity from 1.8 kW to 5.6 kW, in 6 sizes, ind. Type 42VD_H112002011

- Concealed ducted unit medium static pressure, capacity from 2.2 kW to 14.0 kW, in 10 sizes, ind. Type 42VD_H112013010/1

- Concealed ducted unit, High static pressure, capacity from 7.1 kW to 28.0 kW, in 9 sizes, ind. type 42VD_H112011010

- Under Ceiling/floor unit, capacity from 3.6 kW to 16.0 kW, in 7 sizes, ind. type 42VF_H112000010

- Floor standing unit, capacity from 2.2kW to 8.0 kW, in 7 sizes, ind. type 42VS_H112002010

- Conseald floor standing unit, capacity from 2.2kW to 8.0 kW, in 7 sizes, ind. type 42VS_H112003010

- Console, floor standing unit, , capacity from 2.2 kW to 4.5 kW, in 4 sizes, ind. type 42VC_H112000010

- Wall-mounted unit, capacity from 2.2kW to 9.0 kW, in 8 sizes, ind. type 42VH_H112000101 & 42VH_H112000102

All indoor units shall be supplied with single -phase 220-240V-1Ph-50Hz power with earthing.

- Indoor units heat exchanger

The heat exchangers of the indoor units shall be manufactured at the factory using specially configured coper tubes, suitable for R410A refrigerant, mechanically expandable to multiple aluminum fins. The surface of the fins shall be covered by a dual synthetic hydrophilous layer that shall ensure protection from corrosion and better condensate diffusion. The exchanges shall have a suitable total surface for maximization of temperature exchange, while keeping low noise levels.

- Electronic expansion valves

The electronic expansion valves of the indoor units shall be welded at the factory at the entrance of the exchanger and they shall regulate the flow of the refrigerant.

CONTROLLERS

- Local Controllers

Each indoor unit shall be controlled by a wireless controller. It shall also be possible to connect it to a wired local controller.

Up to 12 indoor units may be controlled via a local wired or wireless controller.

It shall also be possible to use the temperature sensor on the local wired controller.

- Central Controller

It shall also be possible to control each system and/or group of systems using local controllers in parallel with group controllers.

Central controllers shall be provided as follows:

- Central ON-OFF controller, control of up to 16 indoor units (indicative type KJR-90B).

- Schedule timer, control of up to 64 indoor units (indicative type WCRF-10-CM).

- Outdoor Centralized Monitor, control of up to 8 systems & 32 outdoor units
(indicative type CRC-10-CM).

The controller shall provide information of the operational status of outdoor units, temperature, voltage, pressure, etc.

- Central remote controller (indicative type CRF-30-CM-B), with touch buttons, can be connected and control up to 64 indoor units.

To summarize, the functionalities per indoor unit are as follows:

Setting & ON/OFF indication.

Setting & mode indication (automatic / heating / cooling /humidification / fan).

Setting & desired temperature indication.

Setting & fan speed indication.

Setting & louvre movement indication (for units with such a function).

Operating schedule

Lock function

Filter status indication and reset.

Error code indication and reset.

Connection to BMS option.

- Central control software

- IM (Intelligent Manager)

Overall control of the systems is offered, based on monitoring all of the systems' functions and adapted to the needs of each building.

A computer and the software shall allow for control of up to 64 systems, 1.024 indoor units, up to 256 outdoor units.

Basic features

- Web Access

- User-friendly operation;

- Central building monitoring and control

- Energy-saving management;

- SMS modem (optional),

- Annual schedule control

- Allocation of electricity consumption expenses

(Outdoor consumption measured through Power Meter & send to M-Interface.

Required Power Meter indicative type Carrier CA-DTS634).

- Low-load operation indicate

- Generate operational history reports (Daily, weekly, monthly);

- Fault display & Warning message

- Filter replacement reminder;

- Emergency stop and Alarm signal output

- Information shall be provided for each indoor unit, thus allowing the identification of the load among the outdoor units. The operating data shall be stored and presented as graphs.

- Data converter

Possibility of converting system data from the IP protocol to the 485 protocol, providing the TCP/IP

portal to achieve WEB / HTTP / TCP / IP access Cloudvrf.carrier.com.cn

Control of up to 64 external units, in real time, without distance limitations.

- Full communication with energy management and control systems for buildings (BMS) through LonWORKS, BACnet, and Modbus protocols.

Implementation of anti-corrosion protection at the job site

Anti-corrosion protection can be implemented using a special coating based on polyurethane for high flexibility and the presence of aluminum in order to create thermal conductivity and resistance to ultraviolet radiation. Resistance against corrosion reaches 10,000 hours (according to standard ASTM Β117). The anti-corrosion protection system shall be in accordance with the specifications of the "Erichsen" tests (DIN 53156) for air conditioning systems and the thickness of the coating shall exceed 25 micron.

The coating material shall be dispatched directly from the production plant and shall be ready for use without additional mixing or dilution.

Before and after applying the coating, the element shall look like the images in the following photograph

New element	Without protection	With corrosion

protection

With corrosion protection