DESCRIPTION OF THE SYSTEM

Multi-zone, multi-split, air-cooled, direct expansion system, with variable refrigerant flow working with refrigerant R410A.

In general, this system shall consist of one or more interconnected outdoor units and several indoor units, on a single refrigerant piping network. Outdoor units have narrow width and the air exhaust is horizontal.

The system shall operate as a heat pump, in cooling or heating mode and the system's main characteristics are as follows:

- Capacity of oudoor units.

Outdoor units with cooling capacity 12,0 kW (4 HP), 14,0 kW (5 HP), 15,5 kW (6 HP) and 17,5 kW (7 HP).

The number of connected indoor units through a single piping network, shall include up to 15 units of all types and sizes (more than 100 different models). The total output of the indoor units can be from 50% to 130% of the total capacity of the  outdoor unit.

Certificates

The manufacturing plant shall have manufacturing quality certification as per ISO 9001 and environmental management system as per ISO 14001.

The units shall be manufactured in accordance with the following European directives/ regulations:

- Directive 2004/108/EC relating to electromagnetic compatibility.

- Directive 2006/42/EC on machinery.

- Directive (PED) 97/23/EC on pressure equipment.

- OUTDOOR UNITS

All outdoor units shall be assembled at the plant; they shall be made of galvanized iron sheet with electrostatic painting, and shall consist of a separate part of compressors - exchangers.

The unit shall have single or three-phase power supply.

The outdoor units shall range from 4 HP to 7 HP and performance shall be as follows:

| POWER | POWER SUPPLY | INDICATIVE TYPE | COOLING CAPAITY KW | HEATING CAPACITY KW |
| --- | --- | --- | --- | --- |
| 4 HP | 220-240V~50Hz | 38VR004H11201E | 12,3 | 13,2 |
| 5 HP | 220-240V~50Hz | 38VR005H11201E | 14,0 | 15,4 |
| 6 HP | 220-240V~50Hz | 38VR006H11201E | 15,5 | 17,0 |
| 4 HP | 380-415V-3N~50Hz | 38VR004H11901E | 12,3 | 13,2 |
| 5 HP | 380-415V-3N~50Hz | 38VR005H11901E | 14,0 | 15,4 |
| 6 HP | 380-415V-3N~50Hz | 38VR006H11901E | 15,5 | 17,0 |
| 7 HP | 380-415V-3N~50Hz | 38VR007H11201E | 17,5 | 19,0 |

Capacities shall be valid under the following operating conditions:

Cooling:	Indoor Temperature 27οC DB/19oC WB & Outdoor Temperature 35oC DB

Heating: 	Indoor Temperature 20οC DB/19oC WB & Outdoor Temperature 7oC DB/6oC WB

All units shall be equipped with scroll DC inverter compressor.

All outdoor units shall be equipped with their own power and control panel, access to the electrical panel shall be through a detachable metal panel.

The noise level of the outdoor units shall be low. The noise level shall be measured from a distance of 1m horizontally and 1.3 m above the base of an outdoor unit, and shall not exceed the following limits (cooling mode):

| Outdoor Units | Sound pressure level dB(A) |
| --- | --- |
| 4 HP/1-phase | 58 |
| 5 HP/1-phase | 57 |
| 6 HP/1-phase | 57 |
| 4 HP/3-phase | 57 |
| 5 HP/3-phase | 57 |
| 6 HP/3-phase | 57 |
| 7 HP/3-phase | 59 |

The system shall operate under extreme outdoor environmental conditions both for cooling and for heating as follows:

- Cooling mode:	from – 15°C to  + 48°C DB

- Heating mode:	from – 15οC to + 27οC DB

- Heat exchangers

The heat exchangers of the outdoor units shall be manufactured at the factory using specially configured high heat transfer coper tubes, suitable for R410A refrigerant, mechanically expandable to multiple aluminum fins.

- Fans

The fans shall be axial, directly connected to high performance, impermeable and permanent lubrication motors.

The impellers of the fans shall be specially designed and manufactured to ensure minimal disturbance of the air flow between blades, as well as a low noise level.

Outdoor units will have two fans with independent DC inverter motors.

- Safety devices

All outdoor units shall be equipped with the following safety devices:

High and low pressure sensors, fuse switches, automatic compressor motor overload fuse, compressor and fan motor overheating switch, oil chamber electrical resistors, restart cycle timer, temperature, suction pressure and compressor discharge sensors.

- Piping

It shall be possible for the system to have extended piping, specifically:

| Piping length | 4-5-6HP |
| --- | --- |
| Total Pipe Length(Actual) | 100 m |
| Maximum Equivalent Piping length from outdoor unit to the farthest indoor unit | 70 m |
| Pipe Length from the first branch to the furthest indoor unit | 20 m |
| Level difference between IDU~ODU | 30 (20)* m |
| Level difference between IDU~IDU | 8 m |

()*if the outdoor unit is located in a lower position

The piping network can be constructed with Y (joints) or with distributors, four divergence box

The thickness and quality of piping shall be suitable for R410A refrigerant, and in accordance with the manufacturer's manuals.

The refrigerant piping must be clean and nitrogen gas must be used during welding, in order to avoid oxidation inside the pipes.

- Installation of units in the project

The factory guidelines must be followed  when installing the units at the job site. The outdoor units must be installed in such a way as to allow easy access in case of maintenance or repair. There should be no obstacles on the side covers (of the electrical panel). All distances specified by the manufacturer and concerning the smooth operation of the units must be followed, and there must not be any obstacles at the fan exits.

INDOOR UNITS OF THE SYSTEM

The following different types of indoor units shall be available, depending on the use and site of installation:

- One-way ceiling cassette, capacity from 1.8 kW to 7.1 kW, in 7 sizes, ind. type 40VZ_H11200010

- Two-way ceiling cassette, capacity from 2.2kW to 7.1 kW, in 6 sizes, ind. type 40VT_H10200010

- Four-way ceiling cassette 60x60, capacity from 2.2 kW to 4.5 kW, in 4 sizes, ind. type 40VX_H11200010

- Four-way ceiling cassette, capacity from 2.8 kW to 14.0 kW, in 10 sizes, ind. type 40VK_H11200010

- Concealed ducted unit, low static pressure, capacity from 1.8 kW to 5.6 kW, in 6 sizes, ind. Type 42VD_H112002011

- Concealed ducted unit medium static pressure, capacity from 2.2 kW to 14.0 kW, in 10 sizes, ind. Type 42VD_H112013010/1

- Concealed ducted unit, High static pressure, capacity from 7.1 kW to 28.0 kW, in 9 sizes, ind. type 42VD_H112011010

- Under Ceiling/floor unit, capacity from 3.6 kW to 16.0 kW, in 7 sizes, ind. type 42VF_H112000010

- Floor standing unit, capacity from 2.2kW to 8.0 kW, in 7 sizes, ind. type 42VS_H112002010

- Conseald floor standing unit, capacity from 2.2kW to 8.0 kW, in 7 sizes, ind. type 42VS_H112003010

- Console, floor standing unit, , capacity from 2.2 kW to 4.5 kW, in 4 sizes, ind. type 42VC_H112000010

- Wall-mounted unit, capacity from 2.2kW to 9.0 kW, in 8 sizes, ind. type 42VH_H112000101 & 42VH_H112000102

All indoor units shall be supplied with single -phase 220-240V-1Ph-50Hz power with earthing.

- Indoor units heat exchanger

The heat exchangers of the indoor units shall be manufactured at the factory using specially configured coper tubes, suitable for R410A refrigerant, mechanically expandable to multiple aluminum fins. The surface of the fins shall be covered by a dual synthetic hydrophilous layer that shall ensure protection from corrosion and better condensate diffusion. The exchanges shall have a suitable total surface for maximization of temperature exchange, while keeping low noise levels.

- Electronic expansion valves

The electronic expansion valves of the indoor units shall be welded at the factory at the entrance of the exchanger and they shall regulate the flow of the refrigerant.

CONTROLLERS

- Local Controllers

Each indoor unit shall be controlled by a wireless controller. It shall also be possible to connect it to a wired local controller.

Up to 12 indoor units may be controlled via a local wired or wireless controller.

It shall also be possible to use the temperature sensor on the local wired controller.

- Central Controller

It shall also be possible to control each system and/or group of systems using local controllers in parallel with group controllers.

Central controllers shall be provided as follows:

- Central ON-OFF controller, control of up to 16 indoor units (indicative type KJR-90B).

- Schedule timer, control of up to 64 indoor units (indicative type WCRF-10-CM).

- Outdoor Centralized Monitor, control of up to 8 systems & 32 outdoor units
(indicative type CRC-10-CM).

The controller shall provide information of the operational status of outdoor units, temperature, voltage, pressure, etc.

- Central remote controller (indicative type CRF-30-CM-B), with touch buttons, can be connected and control up to 64 indoor units.

To summarize, the functionalities per indoor unit are as follows:

Setting & ON/OFF indication.

Setting & mode indication (automatic / heating / cooling /humidification / fan).

Setting & desired temperature indication.

Setting & fan speed indication.

Setting & louvre movement indication (for units with such a function).

Operating schedule

Lock function

Filter status indication and reset.

Error code indication and reset.

Connection to BMS option.

- Central control software

- IM (Intelligent Manager)

Overall control of the systems is offered, based on monitoring all of the systems' functions and adapted to the needs of each building.

A computer and the software shall allow for control of up to 64 systems, 1.024 indoor units, up to 256 outdoor units.

Basic features

- Web Access

- User-friendly operation;

- Central building monitoring and control

- Energy-saving management;

- SMS modem (optional),

- Annual schedule control

- Allocation of electricity consumption expenses

(Outdoor consumption measured through Power Meter & send to M-Interface.

Required Power Meter indicative type Carrier CA-DTS634).

- Low-load operation indicate

- Generate operational history reports (Daily, weekly, monthly);

- Fault display & Warning message

- Filter replacement reminder;

- Emergency stop and Alarm signal output

- Information shall be provided for each indoor unit, thus allowing the identification of the load among the outdoor units. The operating data shall be stored and presented as graphs.

- Data converter

Possibility of converting system data from the IP protocol to the 485 protocol, providing the TCP/IP

portal to achieve WEB / HTTP / TCP / IP access Cloudvrf.carrier.com.cn

Control of up to 64 external units, in real time, without distance limitations.

- Full communication with energy management and control systems for buildings (BMS) through LonWORKS, BACnet, and Modbus protocols.

Implementation of anti-corrosion protection at the job site

Anti-corrosion protection can be implemented using a special coating based on polyurethane for high flexibility and the presence of aluminum in order to create thermal conductivity and resistance to ultraviolet radiation. Resistance against corrosion reaches 10,000 hours (according to standard ASTM Β117). The anti-corrosion protection system shall be in accordance with the specifications of the "Erichsen" tests (DIN 53156) for air conditioning systems and the thickness of the coating shall exceed 25 micron.

The coating material shall be dispatched directly from the production plant and shall be ready for use without additional mixing or dilution.

Before and after applying the coating, the element shall look like the images in the following photograph

New element	Without protection	With corrosion

protection

With corrosion protection