General Description

R410A multi-zone, reverse-cycle, air conditioning system equipped with DC Inverter compressors and electronic expansion valves fitted on each indoor unit for variable refrigerant flow (VRF) control, designed to exceed the minimum efficiency requirements dictated by EU Regulation 2016/2281. System shall consist of a single or more outdoor units and several indoor units depending on application. Both system outdoor and indoor units shall be connected to a single piping network. System shall be configurable to match various capacity requirements; outdoor unit capacity shall range from 8 to 32 HP (models available for every 2 HP increase). Outdoor units shall be combinable so that a maximum single system rated capacity of 96 HP may be achieved (combinable outdoor units available for every 2 HP increase). Arrays of multiple systems shall be feasible to meet the cooling/heating load requirements of large applications. Up to 64 indoor units shall be able to be connected to a single outdoor unit. A number of different indoor unit types shall be available. System piping shall be such to ensure maximum adaptability to application-specific requirements. System shall be capable of sustaining a piping network up to 175 m long and a level difference of up to 90 m between indoor and outdoor units (should the outdoor unit be located above the highest elevation indoor unit). An option shall be available to increase the maximum level difference to 110 m in applications where the outdoor unit is located below the lowest elevation indoor unit. Each independent VRF system shall be capable of having up to 1,000 m of installed pipping network. The system shall be capable of having up to 40 m of piping between the first branch joint and the furthest connected indoor unit. This shall be able to be extended to 90 m upon request. The acceptable deviation between indoor and outdoor unit rated capacities (diversity) shall depend on the type of indoor units used. The minimum acceptable diversity ratio shall be 50% (i.e. indoor unit rated capacity shall be equal to 50% of the outdoor unit rated capacity). Should standard indoor units be used (i.e. units that work with recirculated air) maximum diversity ratio shall be at least 130%. In applications were fresh-air indoor units are used, maximum diversity ratio shall be at least 100%. Should both standard and fresh air indoor units be used, fresh air unit diversity ratio shall not exceed 30% whilst overall system diversity ratio shall not exceed 100%.

| Ecodesign Requirements for Variable Refrigerant Flow Systems (EU Regulation 2016/2281) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Cooling | January 2018 |  | January 2021 |  |
|  | ηs,c % Primary Energy | SEER | ηs,c % Primary Energy | SEER |
| Cooling-only air to air VRFs | 181 | 4.60 | 189 | 4.80 |
| Heating | ηs,h % Primary Energy | SCOP | ηs,h % Primary Energy | SCOP |
| Heat pump VRFs | 133 | 3.40 | 137 | 3.50 |

Operating Limits

Unit shall meet the following minimum operating limit requirements:

| Operating Conditions | Minimum | Maximum |
| --- | --- | --- |
| Cooling | -5 oC DB | 54 oC DB |
| Heating | -23 oC WB | 24 oC DB |

Directive Compliance

Product to be ISO 9001, ISO 14001, SASO, CE, CB and Eurovent certified. Product shall be Ecodesign 2021 ready and comply with the following directives and standards:

- Machinery Directive 2006/42/EC (MD).

- Electromagnetic Compatibility Directive 2004/108/EC.

- Pressure Equipment Directive 97/23/EC.

Testing

The following equipment tests shall be conducted prior to unit shipping:

- A choke test shall be carried out on refrigerant piping to detect potential obstacles/blockages.

- High-pressure pipework shall be tested at a pressure of 40 bar.

- Electronic leak testing shall be carried out to ensure maximum system refrigerant containment.

- A vacuum test shall be conducted at -101.1 kPa.

- Electrical tests including flash-testing at 1,440V AC to ensure that current leaks above 5 mA are detected.

- Megger tests shall be conducted at 500V DC to ensure resistance levels are above 10 Mohm.

- Earth continuity tests shall also be conducted.

Outdoor Unit

Outdoor units shall be factory-assembled with robust supporting feet, made of powder coated galvanized steel metal sheets. Outdoor unit casing shall be made of 1 mm thick panels with weatherproof protection. Access to critical unit components shall not be hindered by unit casing. Unit arrays shall be interconnected on-site using only connections provided by the manufacturer. Outdoor unit minimum acceptable performance characteristics shall be according to the table given below:

| Capacity Index | Cooling Capacity (kW) | Heating Capacity (kW) | SEER | SEER | SCOP | SCOP |
| --- | --- | --- | --- | --- | --- | --- |
| 8 | 25.20 | 25.20 | 7.70 | 6.40 | 4.11 | 4.17 |
| 10 | 28.00 | 28.00 | 7.54 | 6.15 | 4.11 | 4.17 |
| 12 | 33.50 | 33.50 | 7.28 | 6.47 | 4.51 | 4.57 |
| 14 | 40.00 | 40.00 | 6.22 | 6.17 | 4.31 | 3.96 |
| 16 | 45.00 | 45.00 | 5.98 | 5.92 | 4.31 | 3.96 |
| 18 | 50.00 | 50.00 | 6.85 | 6.11 | 3.80 | 3.77 |
| 20 | 56.00 | 56.00 | 6.54 | 5.97 | 3.80 | 3.77 |
| 22 | 61.50 | 61.50 | 6.35 | 5.58 | 3.80 | 3.77 |
| 24 | 67.00 | 67.00 | 7.00 | 5.96 | 3.86 | 3.95 |
| 26 | 73.00 | 73.00 | 6.51 | 5.89 | 3.86 | 3.95 |
| 28 | 78.50 | 78.50 | 6.22 | 5.66 | 3.86 | 3.95 |
| 30 | 85.00 | 85.00 | 6.10 | 5.80 | 3.84 | 3.98 |
| 32 | 90.00 | 90.00 | 5.90 | 5.60 | 3.84 | 3.98 |

Standard outdoor units shall be anti-corrosion treated, this treatment shall provide suitable protection against exposure to average corrosive conditions. Heavy anti-corrosion protection treatment shall also be available upon request. This option features corrosion-resistant steel metal sheets, fan motors, grills, coil fins, cover panels for control parts, screw nuts and supporting feet. This treatment is deemed sufficient to protect equipment surfaces against corrosive ambient conditions, acidic rain as well as saline atmospheres (near coastal areas) and extend product useful life. The level of anti-corrosion protection that the aforementioned treatment offers to major system components shall be evaluated through the conduction of salt mist, moisture and heating as well as light aging testing. Test requirements shall be according to the information presented in the following table.

| Test | Component | Test Hours (Standard Anti-Corrosion) | Test Hours (Heavy Anti-Corrosion) | Testing Standard |
| --- | --- | --- | --- | --- |
| Salt Mist | Heat Exchanger Aluminium Fins | 72h neutral salt mist | 1000h neutral salt mist 140h acid salt mist | Note 1 |
|  | Refrigeration Circuit Copper/Aluminium Tube | 24h neutral salt mist | 120h neutral salt mist (after insulation paint spraying) | Evaluation based on JIS Z 2371 |
|  | Heat Exchanger Sideboard | 96h neutral salt mist | 240h neutral salt mist | No large area red rust |
|  | Steel Tank | 240h neutral salt mist | 500h neutral salt mist | No body red rust |
|  | Screws & Bolts | 300h neutral salt mist | 720h neutral salt mist | Note 2 |
|  | Internal Screws & Gaskets (including those inside electric control box) | 300h neutral salt mist | 720h neutral salt mist (after silicone grease coating) |  |
|  | Electric Control Box | 96h neutral salt mist | 500h neutral salt mist | Note 3 |
|  | Galvanized Steel Panels | 500h neutral salt mist | 1000h neutral salt mist |  |
|  | Compressor/Motor Bolts | 72h neutral salt mist | 168h neutral salt mist (after silicone grease coating) | Note 2 |
|  | Coil | 72h neutral salt mist | 240h neutral salt mist |  |
|  | Motor | 72h neutral salt mist | 240h neutral salt mist | No red rust |
| Moisture & Heating | Galvanized Steel Panels | 1000h | 2000h | Note 4 |
| Light Aging | Galvanized Steel Panels | 500h | 720h | Note 5 |

The board and other major electric components of units with heavy anti-corrosion protection shall be coated with moisture-proof varnish. All galvanized steel panels except for the sideboard shall be zinc-coated (180 g/m2 or greater). Motor shaft shall be made of stainless steel.

In applications where an array of outdoor units is installed, each outdoor unit shall be able to operate as the system main unit. The operation of the outdoor units shall alternate cyclically to extend the useful lifetime of the overall system. Should a fault occur in one of the outdoor units of the array, the system shall be capable of remaining operative using the other outdoor units. Should a fault in one of the compressors of the outdoor unit occur, the system shall be capable of remaining operative using the other compressor. All outdoor units shall be equipped with their own power supply and control panel. Access to the electric box shall be realized through a detachable metal panel. Outdoor units shall have a three-phase power supply, including neutral and earthing; voltage: 400(380-415)V/50Hz.

The acoustic performance of both individual units and outdoor unit arrays shall be according to the table given below. Sound pressure level readings shall be taken from a distance of 1 m (horizontally) and 1.3 m above the base of an individual outdoor unit or outdoor unit array. A “night silent” operating mode shall be available and easily configurable using the outdoor unit’s printed circuit board (PCB). The mode shall include various scheduling options that may be used to reduce unit-generated noise. Night silent mode shall be activated either six or eight hours after ambient peak temperature and deactivated after eight, ten or twelve hours of use. During night silent operating mode, unit noise shall be at least 12 dB(A) lower than in normal operating mode.

| System Index Capacity | Maximum Acceptable Sound Pressure Level [dB(A)] | System Index Capacity | Maximum Acceptable Sound Pressure Level [dB(A)] |
| --- | --- | --- | --- |
| 8 HP | 58 | 54 HP | 66 |
| 10 HP | 58 | 56 HP | 66 |
| 12 HP | 60 | 58 HP | 66 |
| 14 HP | 60 | 60 HP | 66 |
| 16 HP | 61 | 62 HP | 66 |
| 18 HP | 62 | 64 HP | 66 |
| 20 HP | 63 | 66 HP | 67 |
| 22 HP | 63 | 68 HP | 67 |
| 24 HP | 64 | 70 HP | 67 |
| 26 HP | 64 | 72 HP | 67 |
| 28 HP | 64 | 74 HP | 68 |
| 30 HP | 64 | 76 HP | 68 |
| 32 HP | 64 | 78 HP | 68 |
| 34 HP | 65 | 80 HP | 68 |
| 36 HP | 65 | 82 HP | 68 |
| 38 HP | 65 | 84 HP | 68 |
| 40 HP | 65 | 86 HP | 68 |
| 42 HP | 66 | 88 HP | 68 |
| 44 HP | 66 | 90 HP | 68 |
| 46 HP | 66 | 92 HP | 68 |
| 48 HP | 66 | 94 HP | 68 |
| 50 HP | 66 | 96 HP | 68 |
| 52 HP | 66 |  |  |

System Features & Characteristics

Energy Management System

Outdoor unit shall be capable of automatically adjusting the refrigerant evaporating temperature, allowing for the use of higher evaporating temperatures when load requirements in the conditioned space are met. This function shall enable energy-saving and comfortable cooling/heating operation. Unit shall also be able to control the maximum capacity output (40 to 100%) by limiting power consumption. This operation is aimed at reducing power consumption in applications where temporary electricity supply restrictions are in place. Unit shall still be able to provide basic cooling/heating operation should this function be activated.

Electric Component Protection

Unit shall be equipped with a phase sequence detection circuit to allow for the protection of main unit components should power supply terminals be wired incorrectly.

Continuous System Operation during Indoor Unit Repair

System operation shall not be interrupted during indoor unit repair. In case of indoor unit malfunction, power shall be cut off to that particular unit leaving all other indoor and outdoor units unaffected.

Refrigerant Charge Monitoring

System shall be able to monitor the amount of refrigerant present in the cooling circuit of the unit. Unit shall be able to detect in real-time refrigerant over- and under-charging and produce an alarm for the rectification of the issue.

Defrosting

Defrosting operation shall be controlled based on ambient, evaporator and condenser temperature readings as well as outdoor unit running time to eliminate unnecessary defrosting unit operation.

Unit Auto-Addressing

Outdoor units shall assign addresses to indoor units automatically, simplifying system commissioning. Remote and wired controllers shall be used to modify indoor unit addresses accordingly.

Refrigerant-cooled Electric Control

Electric control parts shall be allowed to cool down by allowing refrigerant to flow through them. This technology shall decrease the average temperature of electrical components by about 10 Celsius degrees thus ensuring the stable and safe operation of the control system.

Non-Polarity Communication Wiring (optional)

Unit shall be able to be equipped with a non-polarity indoor-outdoor unit communication wiring. This option shall simplify system commissioning process.

Automatic Refrigerant Charging (optional)

Outdoor unit shall be able to be charged with the appropriate amount of refrigerant automatically. Installer need simply connect the refrigerant charging apparatus to the unit and with a push of a button integrated on the PCB the appropriate amount of refrigerant shall be transferred from the tank to the unit. This function needs to be customized in order for the correct of amount of refrigerant to be charged.

Refrigerant Recovery (optional)

To simplify unit servicing, the refrigerant recovery option shall be activated prior to service when either indoor or outdoor units present malfunctions. In case of indoor unit failure, refrigerant shall be recovered to the outdoor unit/-s. In case of outdoor unit failure, refrigerant shall be either recovered to a different outdoor unit or, should no other outdoor unit be installed, to an interconnected refrigerant tank.

One-Button Commissioning

System shall be able to able to initiate commissioning sequence with a push of a single button. Commissioning sequence shall include piping and wiring checks, refrigerant charging detection and simultaneous system diagnosis (electronic expansion valve, sensor and compressor control etc.).

Dust & Snow Removal

Unit shall be able to control fan operation to remove dust and snow from outdoor unit. This shall allow for the reliable and efficient system operation.

Piping Kits

Branch joints and headers shall be supplied by the manufacturer of the VRF system and shall be used to reduce imbalances in refrigerant flow between indoor units.

Outdoor Unit Components

Compressors

Outdoor units shall be equipped with electronically controlled scroll-type DC Inverter compressors running on FVC68D oil with Enhanced Vapour Injection (EVI) function. Compressors shall comply with CE standard EN 60335-2-40. Compressors shall be equipped with 3-phase, 4-pole, direct start type, synchronous DC motors. Motors shall have a rotating speed range of 15 to 140 rps which implies a running frequency range of 45 to 420 Hz. Compressor motors shall be capable of changing component rotation speed linearly to adjust to the variation of cooling/heating load requirements. Minimum motor insulation class shall be E.

All compressors shall be fitted inside the outdoor unit casing on anti-vibration mounts. To prevent the operation of compressors with no lubrication, a dynamic oil balancing system shall be fitted to the inlet side and a large surface area oil separator shall be placed on the component outlet side. An automatic oil return cycle for the entire system network shall be periodically activated by the micro-processor controller. The compressor, the electrical and thermal motor protection as well as the oil heating system shall all be controlled by the micro-processor controller. Each compressor shall be equipped with multiple protection systems that shall enable the constant monitoring of operating parameters such as compressor current, pressure and temperature.

Refrigerant Circuit

A number of solenoid valves shall be used to ensure precise refrigerant control as well as stable and efficient operation. A plate heat exchanger shall be fitted to the refrigeration circuit to improve refrigerant sub-cooling. This shall allow for higher system efficiencies. Four-way valves shall be used to control refrigerant flow, switching between cooling and heating mode accordingly. Electronic expansion valves (EXV) shall be used to control refrigerant pressure.

Solenoid valves shall also be used to protect the compressor. Should compressor discharge temperature get too high, the solenoid valve shall open and spray a small amount of refrigerant to cool down the compressor. Solenoid valves shall be used to return oil to the compressor, hence ensuring that compressor oil is always kept at a safe level. They shall also be used to enable prompt unit defrosting, shortening the refrigerant cycle and accelerating the defrosting process. Solenoid valves shall be used to allow refrigerant to bypass the expansion valves hence protecting the compressor from high operating temperatures. They shall also be used to allow refrigerant to return directly to the compressor thus avoiding frequent compressor on/off cycles during low system loading.

Fan motors

The outdoor unit fan shall be inverter-driven and operate electronically by monitoring system discharge pressure and loading rate. Fan motors shall adopt a 35-step vector control. Minimum motor insulation class shall be E. Motor shall have IP23 protection class and comply with CE EN 60335-2-40 standard.

Fans

Fans shall be made of fiberglass and acrylonitrile styrene (AS). Fan guide and protective grilles shall be designed for safe vertical air discharge. In dual-fan outdoor units, fans shall feature anti-vibration fan impeller design to achieve quiet operation and large air volumes for greater heat exchanger efficiency. Fan available static pressure shall be at least
60 Pa.

Heat exchanger

Heat exchanger coils shall feature hydrophilic fins and internally threaded copper pipes to optimize component performance. Heat exchangers shall be designed to achieve greater refrigerant sub-cooling for enhanced thermodynamic efficiency. On-site implemented anti-corrosion coating protection shall be available for applications where corrosive ambient conditions are prevalent. Anti-corrosion coating shall contain polyurethane and aluminium in order to enhance thermal conductivity and resistance to ultraviolet radiation degradation. Corrosion-resistance shall be noted according to ASTM Β117 standard requirements. Anti-corrosion protection shall comply with the requirements of DIN 53156.Coating thickness shall exceed 25 microns. Anti-corrosion coating shall be evenly distributed on coil surfaces to ensure uniform protection. Coating material shall be ready-to-use and no additional mixing with secondary anti-corrosion elements shall be required. Indicative schematics of coils with and without anti-corrosion coil protection are given below.

| Newly Purchased Coil | Non-protected Coil | Anti-corrosion Coated Coil |
| --- | --- | --- |

Safety devices

High pressure sensors shall be used to monitor unit discharge. Discharge pressure readings shall then be sent to main PCB where the control system shall regulate the rotation speed of the motor based on system load and discharge pressure. This shall ensure system optimum performance, increasing reliability and lifespan. High- and low-pressure switches shall be used to protect the system from abnormally high and low operating pressures. They shall also protect the compressors from transient pressure spikes and drops. Should system pressure rise or fall below a pre-determined value, the high- or low-pressure switch shall turn the unit off. Ambient and discharge temperature sensors as well as heat exchanger and inverter module temperature sensors shall be used to drive the control system and ensure smooth unit operation.

Indoor Units

Cassettes

Cassettes shall be available in different types: one-way, two-way, compact four-way and four-way cassettes shall be available for different application requirements. Unit fan shall be statically and dynamically balanced to ensure low noise and vibration-free operation. Fan shall feature 7-speed control settings to meet user demands. Heat exchanger coils shall be manufactured from copper tubes mechanically expanded into aluminium fins. They shall be equipped with an electronic expansion valve to control refrigerant flow in response to system load variation. The expansion valve shall be controlled by a computerized proportional–integral–derivative (PID) control system to maintain constant room temperature. A condensate drain pump with at least a 500 mm pump head shall be fitted. Condensates shall be drained from the unit using a suitable evacuation tube. Washable air filters shall also be included.

Ducted Units

Unit casing shall be manufactured from galvanized steel metal sheets, fully insulated. Multi-blade, dual-suction type supply fans, statically and dynamically balanced to ensure low noise and vibration free-operation shall be used. Fan shall feature 7-speed control settings to meet user demands. Fan available static pressure shall be adjustable, ranging between 0 and 280 Pa at various speeds so that the unit may be connected to any duct network. Heat exchanger coils shall be manufactured from copper tubes mechanically expanded into aluminium fins. They shall be equipped with an electronic expansion valve to control refrigerant flow in response to system load variation. The expansion valve shall be controlled by a computerized proportional–integral–derivative (PID) control system to maintain constant room temperature. A condensate drain pump with at least a 500 mm pump head shall be fitted to all units with a rated capacity of less than 16 kW. Condensates shall be drained from the unit using a suitable evacuation tube.

Wall Mounted Units

Unit casing shall be manufactured from heat resistant plastic. Unit support frames shall be made of galvanized steel metal plates. Multi-blade, cross-flow type supply fans, statically and dynamically balanced to ensure low noise and vibration-free operation shall be used. Fan shall feature 7-speed control settings to meet user demands. Heat exchanger coils shall be manufactured from copper tubes mechanically expanded into aluminium fins. They shall be equipped with an electronic expansion valve to control refrigerant flow in response to system load variation. The expansion valve shall be controlled by a computerized proportional–integral–derivative (PID) control system to maintain constant room temperature.
A condensate drain pump shall be fitted along with a suitable evacuation tube for the removal of condensates. Option to add an additional external condensate drain pump shall be available. Washable air filters shall also be included.

Ceiling/Floor Units

Unit shall either be installed horizontally (on the ceiling) or vertically (against the wall) to provide installation flexibility. Unit casing shall be made of heat resistant plastic. Unit fan shall be statically and dynamically balanced to ensure low noise and vibration-free operation. Fan shall feature 7-speed control settings to meet user demands. Heat exchanger coils shall be manufactured from copper tubes mechanically expanded into aluminium fins. They shall be equipped with an electronic expansion valve to control refrigerant flow in response to system load variation. The expansion valve shall be controlled by a computerized proportional–integral–derivative (PID) control system to maintain constant room temperature. Washable air filters shall also be included.

Floor Standing Units

Unit shall be either with or without casing. The air intake of units with casing shall be configurable (either front or underside air intake) to provide unit installation flexibility. Unit casing shall be made of heat resistant plastic. Unit envelope (for units with no casing) shall be made of galvanized steel plates. Unit fan shall be statically and dynamically balanced to ensure low noise and vibration-free operation. Fan shall feature 7-speed control settings to meet user demands. Heat exchanger coils shall be manufactured from copper tubes mechanically expanded into aluminium fins. They shall be equipped with an electronic expansion valve to control refrigerant flow in response to system load variation. The expansion valve shall be controlled by a computerized proportional–integral–derivative (PID) control system to maintain constant room temperature. Washable air filters shall also be included.

Fresh Air Units

Units shall operate on 100% fresh air and shall either be used independently or in conjunction with other types of indoor units. Unit casing shall be made of galvanized steel plates, fully insulated. Multi-blade, dual-suction type supply fans, statically and dynamically balanced to ensure low noise and vibration free-operation shall be used. Fan available static pressure shall be at least 50 Pa on highest fan speed setting. Fan available static pressure shall be adjustable across different speed settings, ranging between 30 and 280 Pa at various speeds so that the unit may be connected to any duct network. Heat exchanger coils shall be manufactured from copper tubes mechanically expanded into aluminium fins. They shall be equipped with an electronic expansion valve to control refrigerant flow in response to system load variation. The expansion valve shall be controlled by a computerized proportional–integral–derivative (PID) control system to maintain constant room temperature.

Heat Recovery Ventilators

Heat exchange medium shall be made of treated paper, suitable for both sensible and latent heat recovery. Heat recovery section sensible efficiency shall be at least 74% whilst recuperator enthalpic efficiency shall be at least 76%. Unit shall be able to be controlled alongside other VRF indoor units. Multiple unit operating modes (heat exchange, bypass, supply air, exhaust air and auto mode) shall be available to meet various user demands.

Commissioning & Testing

System commissioning shall be carried out by a trained engineer under the supervision of the supplier. The entire refrigerant network shall be pressurized with nitrogen at 4 MPa for a period of at least 24 hours. Leak testing shall be carried out with a calibrated electronic leak detector or similar technology equipment should the VRF system fail to maintain constant pressure during testing. Upon successful completion of the aforementioned pressure test, nitrogen shall be allowed to escape from the pipping network. A vacuum pump shall be fitted to VRF pipping to remove air and moisture that would otherwise damage the compressors should the unit be allowed to operate without being previously vacuumed. Vacuum pump shall be set at -101.1 kPa. Pipping network shall be held at negative pressure (-101.1 kPa) for at least 2 hours with switched off vacuum pump(s). Refrigerant shall then be charged to the liquid pipe (in liquid state). Required system refrigerant charge shall be determined based on selected outdoor and indoor units as well as pipping network length using a selection software provided by system manufacturer.

Control

Remote Controllers

Local control shall be provided using remote controllers mounted within the occupied space. These controllers shall be able to provide at least the following functions: individual unit start/stop, mode selection, temperature setting, fan speed adjustment, keyboard lock, louver swing control and timer setting. The controller shall include an internal temperature sensor which shall be used for system control.

Communication Protocols

BMS Gateway

Manufacturer shall provide a Building Management System (BMS) gateway to enable communication between the VRF system and third party BMSs.

BACnet Gateway

Device shall be able to monitor and control a maximum of 256 indoor or 96 outdoor units. List of minimum acceptable available features is given below:

- Up to 256 indoor or 96 outdoor units shall be controlled by the BACnet gateway.

- Air conditioners shall be operated and monitored using the BACnet central board.

- System shall be able to monitor indoor unit malfunctions.

- System shall be able to monitor and change temperature setpoints.

- System shall be able to monitor indoor space temperature variations.

- System shall be able to switch unit operating mode and indoor unit fan speed.

- System shall be able to lock remote controllers.

LonWorks Gateway

Device shall be able to monitor and control a maximum of 64 indoor units. List of minimum acceptable available features is given below:

- Up to 64 indoor units shall be controlled by the LonWorks gateway.

- Air conditioners shall be operated and monitored using the LonWorks central board.

- System shall be able to monitor indoor unit malfunctions.

- System shall be able to monitor and change temperature setpoints.

- System shall be able to monitor indoor space temperature variations.

- System shall be able to switch unit operating mode and indoor unit fan speed.

Modbus Gateway

Device shall be able to monitor and control a maximum of 64 indoor and 3 outdoor units. List of minimum acceptable available features is given below:

- Up to 64 indoor and 3 outdoor units shall be controlled by the Modbus gateway.

- Air conditioners shall be operated and monitored using the Modbus central board.

- System shall be able to monitor indoor unit malfunctions.

- System shall be able to monitor and change temperature setpoints.

- System shall be able to monitor indoor space temperature variations.

- System shall be able to switch unit operating mode and indoor unit fan speed.

- System shall be able to provide unit scheduling options (timer setting).

- System shall be able to lock remote controllers.

ηs,c=SEER kWhkWh×1002.50-icorrections

ηs,h=SCOP kWhkWh×1002.50-icorrections

Cooling Capacity measured at: Indoor Temperature 27οC DB/19oC WB & Outdoor Temperature 35oC DB.

Heating Capacity measured at: Indoor Temperature 20οC DB/19oC WB & Outdoor Temperature 7oC DB/6oC WB.

SEER determined when outdoor unit is connected to ducted indoor units.

SEER determined when outdoor unit is connected to 4-way cassette indoor units.

SCOP determined when outdoor unit is connected to ducted indoor units.

SCOP determined when outdoor unit is connected to 4-way cassette indoor units.

Evaluation according to ASTM B117 NACL 5%, 35°C. Under trichloroethylene 85°C, 5 min, weight loss < 1%.
	Under perchloroethylene 120°C, 30 min, weight loss < 1%.

Evaluation according to following criteria: No significant colour and lustre change, no corrosion on coating surface
  	greater than 3% of total surface area, no corrosion and red rust on component surface.

No visible rusting, blistering and cracking of component surface. Minor colour change and coating peel-off
	acceptable only in proximity to connections with other components.

No rust and visible coating peel-off under a 10- times magnifying glass.

Q-U-V testing according to ASTM G87. Cyclic testing with UV-A light (wavelength of 313 nm). Testing at 60°C x 4h
      	followed by 40°C x 4h.